## Grand Summary
Schedule 7 STP : Grand Summary of Bytrayanapura Zone
Name of STP
Local Component
Page | Schedule No. | Description | Local Currency (INR) | GST | PRICE
Schedule 1 | SEWER 1 | Bytrayanapura Zone1 | 112749620 | 0 | 0
Schedule 2 | SEWER 2 | Bytrayanapura Zone2 | 112650329 | 0 | 0
Schedule 3 | SEWER 3 | Bytrayanapura Zone3 | 132308517 | 0 | 0
Schedule 4 | SEWER 4 | Bytrayanapura Zone4 | 154507853 | 0 | 0
Schedule 5 | SEWER 5 | Bytrayanapura Zone5 | 409983928 | 0 | 0
Pumping | Pumping Main | Bill of Quantities for Pumping Main for Bytrayanapura Zone | 19826987 | 0 | 0
SOD | Day Works | Bill of Quantities for Day Works for Bytrayanapura Zone | 17291500 | 0 | 0
| 7 | GRAND TOTAL FOR Bytrayanapura Zone | 959318734 | 0 | 0
Signature of Bidder
Name & Designation
Company

## Schedule 1
SEWER 1: Bill of Quantities for Sub-mains and Trunk Lines of Chikkabettahalli and Doddabettahalli Villages of Bytrayanapura Zone-1
Level | Item No. | Description | Quantity | Units | Rate (INR) | Duties | Ex.Work | Local Transport | GST | Amount (INR)
2 | 1 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN ALL KINDS OF SOIL MIXED WITH BOULDERS of 30cm size upto and exclusive of disintegrated rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following
3 | a | IN ALL KINDS OF SOIL MIXED WITH BOULDERS
4 | i | 0 to 2 Mts. Depth | 14619 | Cum | 265 |  |  |  |  | 3874035
4 | ii | 2 to 4 Mts. Depth | 8745 | Cum | 305 |  |  |  |  | 2667225
4 | iii | 4 to 6 Mts. Depth | 1497 | Cum | 340 |  |  |  |  | 508980
4 | iv | 6 to 8 Mts. Depth | 161 | Cum | 400 |  |  |  |  | 64400
3 | b | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN DISINTEGRATED ROCK, SOFT ROCK, SOFT SHALE AND MEDIUM HARD ROCK COMPRISING OF LIME STONE, SAND STONE, HARD SHALE, SCHIEST, FISSURED ROCK including all types of laterite without resorting to blasting or as directed including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 3656 | Cum | 345 |  |  |  |  | 1261320
4 | ii | 2 to 4 Mts. Depth | 2187 | Cum | 392 |  |  |  |  | 857304
4 | iii | 4 to 6 Mts. Depth | 375 | Cum | 442 |  |  |  |  | 165750
4 | iv | 6 to 8 Mts. Depth | 41 | Cum | 4 |  |  |  |  | 164
3 | c | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. in hard rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 2011 | Cum | 1260 |  |  |  |  | 2533860
4 | ii | 2 to 4 Mts. Depth | 1204 | Cum | 1400 |  |  |  |  | 1685600
4 | iii | 4 to 6 Mts. Depth | 206 | Cum | 1900 |  |  |  |  | 391400
4 | iv | 6 to 8 Mts. Depth | 23 | Cum | 2200 |  |  |  |  | 50600
3 | d | Excavation of hard rock by using Machinery like Generator, Hitachi, Breaker, Compressor, Diamond Rope with MS rods or as directed etc. with all lead and lift complete as per specifications and drawings and as directed including utility restoration, clearing and grubbing with all lead and lift as per drawings & specification and as directed | 1252 | Cum | 4462 |  |  |  |  | 5586424
2 | 2 | Providing, erecting and removing casurina pole three tier BARRICADING using poles of 7.5 to 10 cms dia or as required and minimum 1.5M height above ground fixed vertically at intervals of 2.0 to 2.5 M centre to centre or as required and horizontally at 0.5M above ground level or as required, including fixing poles in ground for a maximum depth of 0.3M and tied with coir rope firmly including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed | 7753 | Rmt | 44 |  |  |  |  | 341132
2 | 3 | Refilling of available earth around pipelines, in layers not exceeding 20 cms in depth, compacting each deposited layer by ramming after watering all lead and lift including cost of all labour including consolidation by mechanical or manual means as approved by Engineer, when earth is at suitable moisture content with desired field density upto 95% maximum dry density (modified heavy proctor test) for restoration of roads without settlement including HOM of machineries, complete. (The contractor shall take care while consolidating the earth, so that, pipes laid are not damaged due to mechanical compaction and shall restore the damaged pipes at his own cost, in case of damage) with all lead and lift and as directed complete | 26803 | Cum | 110 |  |  |  |  | 2948330
2 | 4 | Extra charges for excavation in all classifications in watery situations or foul conditions as under towards dewatering with all recuperation rates with all lead including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed until completion of the works for the following - 0 to 2 Mtr. Depth | 7750 | Cum | 52 |  |  |  |  | 403000
3 | a | 2 to 4 m depth | 2702 | Cum | 78 |  |  |  |  | 210756
3 | b | 4 to 6 m depth | 404 | Cum | 104 |  |  |  |  | 42016
3 | c | 6 to 8 m depth | 30 | Cum | 130 |  |  |  |  | 3900
2 | 5 | Cutting road surface for pipeline trenches as per specifications and as directed and including disposing off the unserviceble excavated stuff as directed including barricading, danger lighting etc, in the following classifications with all lead and lift and as directed for the following | [7 empty] | 0
3 | a | Cutting asphalt road | 1609 | Cum | 759 |  |  |  |  | 1221231
3 | b | Cutting CC Road | 403 | Cum | 1150 |  |  |  |  | 463450
2 | 6 | Providing and laying Plain Cement Concrete 1:2:4 of specified grade for foundations (screed layer) with 20 mm and down size of approved gradation hard broken granite, trap basalt or with any other approved hard aggregate including cost and conveyance of all materials, lead and lifts, plywood / steel form works, machine mixing, laying, tamping, curing etc. complete and as per specification and as directed for the following | [7 empty] | 0
3 | a | For Bedding of Sewer Pipes and other works | 414 | Cum | 4000 |  |  |  |  | 1656000
2 | 7 | Providing and laying plain/reinforced cement concrete for side drains using M20 nominal mix concrete with OPC at minimum 300 kgs with 20 mm and down size granite metal coarse aggregates at 0.69 cum and fine aggregates at 0.43 cum as per desing mix, machine mixed, well compacted for walls and bottom including centering, shuttering, cost of materials, HOM of machinery, curing etc., complete including cost of admixuture excluding cost of steel as per MORTH specification No. 1500, 1700, 2200. including cost of materials, labour, HOM complete as per specifications for raft and walls of SWD works or other works as directed | 62 | Cum | 6189 |  |  |  |  | 383718
2 | 8 | Providing and laying cement concrete 1:1.5:3 proportion for RCC works of raft, footings, encasing of pipes or other works as directed with 20 mm and down size of approved gradation hard broken granite, trap, basalt or with any other approved hard aggregate including machine mixing, cost and conveyance of all materials with all lead and lifts including plywood / steel form work, machine mixing, laying in layers of 15 cm, compacted, curing, smooth finishing etc. complete with all lead and lift and as directed (excluding the cost of reinforcement). For Encasement | 503 | Cum | 5025 |  |  |  |  | 2527575
2 | 9 | KSRB 4-9.2: Providing TMT Fe 500 steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications with all lead and lift complete. Specification No. KBS 4.6.3 | 37375 | Kgs | 50 |  |  |  |  | 1868750
2 | 10 | KSRRB M700-4. Providing and Laying Boulder Apron in Crates of Synthetic Geogrids:- Providing, preparing and laying of geogrids crated apron of required thickness including excavation and backfilling with geogrids having characteristics as per clause 700.4.2, joining sides with connectors/ring staples or as required, top corners to be tie tensioned or as required, placing of suitable cross interval ties in layers of 300 mm or as required connecting opposite side with lateral braces and tied with polymer braids to avoid bulging, constructed as per clause 700.4.3. filled with stone as per specification for providing aroud the sewer pipe for pipe bedding/anchoring and as per specifications. For Pipe bedding in water logged area | 100 | Cum | 3700 |  |  |  |  | 370000
2 | 11 (a) | Providing Precast anti floatation blocks of RCC M20 grade concrete including casting at yard, including cost of reinforcement, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site, including providing and fixing of anchor bolts during precasting including cost of erection of anti floatation block below the sewer pipe and fixing of the steel strips as per requirement (including cost of steel strip for fixing of minimum 32mm wide and minimum 8 mm thick) including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 20 | Cum | 5550 |  |  |  |  | 111000
2 | b | Providing, driving and anchoring minimum 8 mm diameter minimum HYSD FE 500 reinforcement including cost of bending, driving, sharpening the edge for driving including cost of material, labour and other materials required as per drawings and specifications and as directed by the Engineer for holding the pipe in uplift situations complete with all lead and lift as per specification and as directed | 74 | m | 45 |  |  |  |  | 3330
2 | c | Providing Pre cast anti floatation slabs of RCC M20 grade concrete including casting at yard, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site including cost of steel strip of minimum 32mm wide and minimum 8 mm thick including providing and fixing of lifting hooks anchor bolts during precasting and nuts including cost of erection of anti floatation slabs below the sewer pipe and fixing of the steel strips as required including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 19 | Sqm | 5550 |  |  |  |  | 105450
2 | 12 | Providing and removing shoring and strutting for protecting both sides of pipe line trenches, where ever required, including the cost of all required materials and labour, safety requirements, including maintaining the shoring until completion of works complete as per specification NO.KBS 2.5/2.13 (for both sides single measument will be taken) with all lead and lift and as per the direction of the engineer complete | 9440 | Sqm | 460 |  |  |  |  | 4342400
2 | 13 | MS Sheet Piling - Providing and installing sheet piling for both sides of the trench for following depths, with Mild Steel Sheets not less than 6.5mm thick, stronger knife edge, recessed spreader sockets, 3" single or double wall shields, to be designed by the contractor to withstand all types of soils, maximum depths of as per the approved design drawing, including labour charges for installing and removing the sheet piling at various reaches of sewer line construction, including loading, unloading, transporting to the suitable location etc., complete with all lead and lifts (Measurement shall be taken for one side only even though it is provided for both sides) and maintaining the sheet piling until completion of works complete Above 3m Depth | 2360 | Sqm | 675 |  |  |  |  | 1593000
2 | 14 | Supplying DOUBLE WALL CORRUGATED (External annular corrugated & smooth internal wall) (DWC) of class SN 8, S & S piping system in accordance with IS 16098 (Part-2) and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, including rubber rings conforming to IS 5382 and cuts of pipes wherever necessary including jointing with all labour, lead & lifts, complete and giving necessary hydraulic test to the required pressure as per ISS (contractor will make his own arrangements for procuring water for testing) etc. for the following | [7 empty] | 0
3 | a | Pipes of SN 8, 400 mm dia. | 320 | Rmt | 2800 |  |  |  |  | 896000
3 | b | Pipes of SN 8, 500 mm dia. | 322 | Rmt | 4800 |  |  |  |  | 1545600
2 | 15 | Supplying of following diameters S&S RCC SPUN / VIBRATED CAST PIPES (REINFORCED) of NP-3 class conforming to IS 458:1988 with latest amendments manufactured using sulphate resistant cement and conveying to worksite, rolling and lowering into trenches, laying true to line and level including loading and unloading at both destinations and jointing of pipes & specials including cost of specials including perfect linking of joints with jack to correct position including cost of jointing materials i.e., rubber rings confirming to IS : 5382 for S&S RCC pipes with all lead and lifts as directed and giving necessary hydraulic test as per ISS and testing & commissioning etc., complete. (Contractor will make his own arrangements for procuring water for testing) including cost of all materials, labour complete as per specification and as directed for the following | [7 empty] | 0
3 | a | 300 | 332 | Rmt | 2250 |  |  |  |  | 747000
3 | b | 350 | 835 | Rmt | 2700 |  |  |  |  | 2254500
3 | c | 400 | 138 | Rmt | 3350 |  |  |  |  | 462300
3 | d | 500 | 2888 | Rmt | 4200 |  |  |  |  | 12129600
3 | e | 700 | 1618 | Rmt | 5800 |  |  |  |  | 9384400
2 | 16 | Providing and laying testing and commissioning of Ductile iron pipes of class-K7 conforming to IS 8329:2000 with latest amendments, conveying to work site, rolling and lowering into trenches, laying true to line, level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, cutting of pipes wherever necessary, jointing with rubber gaskets, cleaning the socket and spigot end with soap solution, applying soft soap to the socket and spigot ends before insertion of rubber gaskets, jacking and fixing in perfect conditions etc. The cost to include soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS with all lead and lifts and cost of all jointing materials. (The contractor will make his own arrangements for water) the internal cement motor linning shall be with High Alumina Cement (HAC) internal cement mortal lining (CML) of DI pipes complete as per specification and as directed with all lead and lift complete for (For Major Storm Water Drain Crossing) for the following | [7 empty] | 0
3 | a | 300 mm dia | 30 | Rmt | 3200 |  |  |  |  | 96000
3 | b | 350 mm dia | 40 | Rmt | 3450 |  |  |  |  | 138000
3 | c | 400 mm dia | 30 | Rmt | 4800 |  |  |  |  | 144000
3 | d | 500 mm dia | 160 | Rmt | 6650 |  |  |  |  | 1064000
3 | e | 700 mm dia | 80 | Rmt | 11000 |  |  |  |  | 880000
2 | 17 | Construction of RCC manhole chambers of RCC M 30 Grade approved type pre-cast RCC manhole chambers, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resitant cement, using RCC M 30 grade proportion with 20mm and downgraded jelly, well graded sand and reinforcement steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of house service connection, incoming and outgoing pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including excavation in all types of soil/rock, dewatering, refilling, sand bedding wherever required, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 18 | nos | 49000 |  |  |  |  | 882000
4 | ii | For every additional 0.1m upto 2m | 169 | nos | 1800 |  |  |  |  | 304200
4 | iii | 2mdepth | 10 | nos | 68000 |  |  |  |  | 680000
4 | iv | For every additional 0.1m upto 3m | 12 | nos | 1900 |  |  |  |  | 22800
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 90 | nos | 74000 |  |  |  |  | 6660000
4 | ii | For every additional 0.1m upto 3m | 720 | nos | 2200 |  |  |  |  | 1584000
4 | iii | 3m depth | 40 | nos | 98000 |  |  |  |  | 3920000
4 | iv | For every additional 0.1m upto 4m | 162 | nos | 2225 |  |  |  |  | 360450
4 | v | 4m depth | 17 | nos | 116000 |  |  |  |  | 1972000
4 | vi | For every additional 0.1m upto 5m | 90 | nos | 2250 |  |  |  |  | 202500
4 | vii | 5m depth | 14 | nos | 125000 |  |  |  |  | 1750000
4 | viii | For every additional 0.1m upto 6m | 86 | nos | 2250 |  |  |  |  | 193500
3 | c | 1.8m Diameter manholes | [7 empty] | 0
4 | i | 6m depth | 4 | nos | 180000 |  |  |  |  | 720000
4 | ii | For every additional 0.1m upto 7m | 26 | nos | 2400 |  |  |  |  | 62400
2 | 18 | Cast in Situ Manholes in Drain/Nallah Edge/Road: Construction of RCC manhole chambers of M30 Grade proportion, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resistant cement, using M30 grade RCC with 20mm and downgraded jelly, well graded sand and steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including sand bedding wherever required, including earthwork in all types of soil/rock, dewatering, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 28 | nos | 74000 |  |  |  |  | 2072000
4 | ii | For every additional 0.1m upto 3m | 215 | nos | 1900 |  |  |  |  | 408500
4 | iii | 3m depth | 10 | nos | 93000 |  |  |  |  | 930000
4 | iv | For every additional 0.1m upto 4m | 43 | nos | 2400 |  |  |  |  | 103200
4 | v | 4m depth | 1 | nos | 130000 |  |  |  |  | 130000
4 | vi | For every additional 0.1m upto 5m | 5 | nos | 3100 |  |  |  |  | 15500
2 | 19 | Providing and fixing DROP ARRANGEMENT with following dia. HDPE grade PE-100 pipes, conforming to PN 6 as per IS 14333 with latest amendments, vertical drop pipe with MS fastenings at 300 mm C/C or suitable materaial as required, with suitable expander / reducer HDPE ‘T’ joint at top with incoming sewer with one end of Tee inside the manhole closed with end cap and 45 degree bend at the bottom with HDPE specials and encasing the pipe outside the manhole with cement concrete 1:2:4 proportion, 150 / 200 mm thick alround the HDPE pipe, including vibrating, compacting, necessary centering and form work, curing, testing etc. including cost and conveyance of all materials, labour with all lead and lifts etc. complete as per specification, drawings and as directed by the Engineer in charge etc. for the followng complete with all lead and lift | [7 empty] | 0
3 | a | For 300 mm dia. incoming sewer pipe. | 5 | Rmt | 8420 |  |  |  |  | 42100
3 | b | For 350 mm to 500 mm dia. incoming sewer pipe. | 69 | Rmt | 13140 |  |  |  |  | 906660
3 | c | For 600 mm to 750 mm dia. incoming sewer pipe. | 25 | Rmt | 26325 |  |  |  |  | 658125
2 | 20 | Dewatering the sewage or other drainage water by using minimum 5 HP pump for the diversion of storm / sewage including cost of machinery, piping upto disposal point, fuel, operator, HOM of machinery complete including diverting to the safe location as per specifications and as per the direction of the engineer with all lead and lift complete | 1056 | Hr | 185 |  |  |  |  | 195360
2 | 21 | Overpumping charges for pumping of sewage for pumping of sewage from u/s manhole to the d/s manholes or as directed including cost of machinery, piping as per site requirement, fuel, operator, HOM of machinery complete as per specifications and as per the direction of the engineer with all lead and lift | 1056 | Hr | 525 |  |  |  |  | 554400
2 | 22 | Providing sewer plugs of required sizes as per site requirement or plugging of manholes with sand / clay bags & other materials as required for the plugging/diversion of sewage from existing manholes including all required safety equipment, approvals complete with all lead and lift and as directed | 65 | nos | 380 |  |  |  |  | 24700
2 | 23 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Dismantling Stone Masonry and Rubble stone Masonry in cement mortar as per the direction of the Engineer | 70 | Cum | 1000 |  |  |  |  | 70000
2 | 24 | Construction of dismatled size stone masonry with available stones including curing and mortar (in CM 1:6) including cost of all other required materials, required labour, machinery, curing complete with all lead and lift and as per specification and as directed | 20 | Cum | 3650 |  |  |  |  | 73000
2 | 25 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Reinforced Cement Concrete grade M20 and above as per the direction of the Engineer | 62 | Cum | 1000 |  |  |  |  | 62000
2 | 26 | KSRB 5-2.3: Providing and constructing granite/trap/basalt size stone masonry in Foundation or as required with cement mortar 1:6, stone hammered dressed in courses not less than 20cm high, bond stones at two m. apart in each course including cost of materials, labour, curing complete as per specifications. Specification No. KBS 5.1.13 complete with all lead and lift and as directed | 50 | Cum | 3650 |  |  |  |  | 182500
2 | 27 | Providing and filling in foundation/trench bottom with granite/ trap broken metal 100mm and down size with stone spalls/boulders to fill the voids, hand roller, ramming including cost of all material and labour with all lead and lifts, complete as per the specification in slushy soil for soling work complete as directed | 103 | Cum | 785 |  |  |  |  | 80855
2 | 28 | Disposing of excavated Earth of all types to a distance of upto average one side distance of 25 kilometers by vehicle including head load where ever required including loading, unloading to approved location with all lifts, labour, HOM of machinery etc. complete as per specification and as directed | 4478 | Cum | 430 |  |  |  |  | 1925540
2 | 29 (a) | Conducting the Level and Strip of Survey of alignment of Main Sewers of diameter 300mm and above, including all data required for generating GIS maps of sewer network, preparation and submission of plan & LS with ground level at 30m interval and junction points along the centre line of the alignment etc., showing the right of way, any permanent features, culverts including providing branch sewer pipeline catment survey & manhole details complete as per specifications and as directed by the Engineer in charge with all lead and lifts etc., complete for the following: for 300 mm dia | 332 | Rmt | 18 |  |  |  |  | 5976
2 | b | Above 300 mm dia | 6121 | Rmt | 25 |  |  |  |  | 153025
2 | 30 | Providing and fixing 150mm dia Cast Iron pipe for ventilating shaft minimum 5m high with specials and cowl and with suitable grips in CC 1:2:4 pillar using 10mm to 20mm graded hard granite/trap/basalt or any other approved metal with 15cms thick cement concrete (1:2:4) around up to 1.22 mtrs above the GLR and with a foundation base of 90x90x90 cms plastered with 12 mm thick CMC 1:3 to all exposed faces and linking the shaft to the manholes by means of 15 cm dia GSW pipes and specials, jointing with tar dipped hemp 1:1½ CM caulking, curing with all lead and lifts etc., complete for all materials earth work excavation and refilling in all strata and disposal of surplus earth as directed with all lead and lifts etc., complete | 2 | nos | 21000 |  |  |  |  | 42000
2 | 31 | Providing gravel bedding for the pipe line trenches using approved granular material of size less than 25mm (murrum) including watering and consolidation by punners etc., complete with all lead and lifts, as per specification and as directed by the Engineer complete | 957 | Cum | 480 |  |  |  |  | 459360
2 | 32 | Providing Bedding or Backfillling using approved stone dust/quarry dust of size not exceeding 5.6mm for the pipe line trenches including watering and consolidation to 95% proctor density etc., complete with all lead and lifts as per specification and as directed by the Engineer complete | 388 | Cum | 799 |  |  |  |  | 310012
2 | 33 | Provide murrum bedding for the pipeline trenches in black cotton and rock reaches or as per site requirement including watering and consolidation by punners etc. complete with all lead and lift and as directed complete | 194 | Cum | 209 |  |  |  |  | 40546
2 | 34 | KSRRB M200-14.1. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications. MORTH Specification No. 202 for Dismantling brick In cement mortar as as per the direction of the Engineer | 50 | Cum | 220 |  |  |  |  | 11000
2 | 35 | KSRB 6-2 : Providing and constructing burnt brick masonry with approved quality of non-modular bricks of standard size of class designation 5.0 Newton per sqmm (table moulded) with cement mortar 1:6 for basement and superstructure including cost of materials, labour charges, scaffolding, curing complete as per specifications. Specification No. KBS 6.2 complete with all lead and lift and as directed by the Engineer | 50 | Cum | 5820 |  |  |  |  | 291000
2 | 36 | Removing B.S. slabs of Drain and stacking with all lead and lifts as directed by the Engineer | 250 | Sqm | 55 |  |  |  |  | 13750
2 | 37 | Refixing of the available stone slabs of drains including other required materials and pointing in C.M. (1:3) with all lead and lifts complete and as directed by the Engineer complete | 250 | Sqm | 67 |  |  |  |  | 16750
2 | 38 | Providing granite slabs of 7.50 cms thick of selected quality roughly dressed and fixed in cement mortar (1:6), including pointing, curing etc complete with all lead and lifts as per specification and as directed by the Engineer . | 200 | Sqm | 548 |  |  |  |  | 109600
2 | 39 | Supplying to work spot rolling, lowering and placing in position RCC perforated rings in the already excavated pit including loading and unloading at both the destinations with all lead and lift etc., complete for soak pits including removal/dismantling of existing soak pits including disposal of unserviseble materials with all lead and lift complete | 10 | Each | 6290 |  |  |  |  | 62900
2 | 40 | Making bore in manholes without damaging the existing manholes, fixing the pipe of any diameter in line and level with CC 1:2:4, plastering the outer and inner surface in CM 1:3 including curing etc. using Sulphate Resistant Cement including disposal of debris. The cost includes the cost of materials, labour charges, lead and lifts etc. complete as per specifications and as directed by the Engineer. | 34 | nos | 180 |  |  |  |  | 6120
2 | 41 | Removing manhole cover and frame carefully and refixing the same in CC 1:2:4 band and finishing as per drawings complete with all lead and lift including disposal of the unserviceble materials complete as directed | 34 | nos | 200 |  |  |  |  | 6800
2 | 42 | Cutting of trees of the following girths, including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in depression/pits etc. including labour charges, all lead and lifts etc. all as per specifications and instructions of the Engineer in charge. MOST specification 201 for the following | [7 empty] | 0
3 | a | For trees of 300 mm to 600 mm girth | 15 | nos | 77 |  |  |  |  | 1155
3 | b | For trees of 600 mm to 1200 mm girth | 15 | nos | 98 |  |  |  |  | 1470
2 | 43 | KSRB M 300-54, Construction of embankment with approved new material with all lead and lift graded and compacted to meet requirement of table 300-2 complete as per Specification which includes watering & compaction by virbratory roller/ramper/plate vibrator. MOSRTH Specification No.305 complete | 1950 | Cum | 185 |  |  |  |  | 360750
2 | 44 | Provide bedding using approved stone dust / quarry dust of size not exceeding 5.6 mm for the pipe lines trenches including watering and consolidation to 95% proctor density etc. complete with all lead and lifts as per specifications and as directed by the Engineer complete | 1950 | Cum | 805 |  |  |  |  | 1569750
2 | 45 | Construction of granular sub-base Grading-V as Sub-base and drainage layer by providing coarse graded crushed stone aggregates of granite/trap/basalt material, mixing by mix in place method by rotavator at OMC, spreading in uniform layers with motor grader on prepared surface and compacting with vibratory power roller to achieve the 98 % proctor density, complete as per specifications. Clause 401 of MORTH V Revision For Grade II Material or as required and directed complete with all lead and lift | 1950 | Cum | 1450 |  |  |  |  | 2827500
2 | 46 | KSRRB M400-14.1. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt of specific sizes to water bound macadam specifications including spreading in uniform thickness, hand packing, rolling with 3-wheeled steel/vibratory roller 8-10 tonnes in stages to proper grade and camber, applying and brooming requisite type of screening/binding materials to fill up the interstices of coarse aggregates, watering and compacting to the required density complete as per Specification. A. By manual means. MORTH Specification No. 404 Type B 11.2mm for grading III complete with all lead and lift complete as per specification and as directed | 196 | Cum | 1625 |  |  |  |  | 318500
2 | 47 | KSRRB M400-17. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt to wet mix macadam specifications including pre mixing the material with water at OMC in mechanical mix plant carriage of mixed materials by tipper to site, laying in uniform layers with paver in sub-base/base course on well prepared surface and compacting with vibratory roller to achieve the desired density complete as per specifications. MORTH Specification No. 406 with all lead and lift complete as per specification and as directed | 781 | Cum | 1800 |  |  |  |  | 1405800
2 | 48 | KSRRB M500-6. Providing and applying primer coat with S.S. bitumen emulsion on prepared surface of granular base such as WMM including cleaning of road surface and spraying primer at the rate of 0.60 kg / sqm using mechanical means complete as per specifications. Clause 502 of MORTH V revision with all lead and lift complete | 5200 | Sqm | 25 |  |  |  |  | 130000
2 | 49 | KSRRB 500-7. Providing and applying tack coat using 80/100 grade bitumen (VG10) on the prepared black topped surfaces at 2.5 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 5200 | Sqm | 11 |  |  |  |  | 57200
2 | 50 | KSRRB 500-9. Providing and applying tack coat using 80/100 grade bitumen (VG10) on granular base such as WBM surfaces hot bitumen primed at 4 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 1301 | Sqm | 17 |  |  |  |  | 22117
2 | 51 | KSRRB 500-11. Providing and laying bituminous macadam on prepared surface with crushed coarse aggregates as per design mix formula for base / binding course including loading of aggregates with F.E. loader, hot mixing of stone aggregates and bitumen in hot mix plant, transporting the mixed material in tipper to paver and laying mixed materials with paver finisher to the required level and grade, rolling by smooth wheeled, vibratory & tandem rollers to achieve the desired density, but excluding cost of primer / tack coat & including lead, lift and cost of all materials, labour, HOM complete as per specifications. Clause 504 of MORTH V revision do - using 40/60 TPH capacity H.M.P. with Mechanical paver Gr-II (50 mm to 75 mm or as directed) with 3.4% VG-30 Bitumen complete with all lead and lift and as directed | 261 | Cum | 6000 |  |  |  |  | 1566000
2 | 52 | KSRB M500-18, Providing and laying semi dense bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause no 508 complete in all respects as per specification with all lead and lift do using 40/60 TPH capacity HMP with Mechanical Paver Gr-II (25 mm to 30 mm or as directed ) with 5% VG-30 Bitumen compelte with all lead and lift and as per specifications | 131 | Cum | 7200 |  |  |  |  | 943200
2 | 53 | KSRRB M500-19. Providing and laying bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler, transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction in all respects complete as per specifications. Clause 507 of MORTH V revision do - using40/60 TPH capacity H.M.P. with Mechanical Paver Gr-II (30 mm to 40 mm or as directed) with 5.4% VG-30 Bitumen compelte with all lead and lift and as per specifications | 66 | Cum | 8000 |  |  |  |  | 528000
2 | 54 | KSRB 4-1.2 : Providing and laying in position plain cement concrete of Mix 1:3:6 with OPC @ minimum 220kgs, with 40mm and down size graded granite metal coarse aggregates @0.892cum and fine aggregates @ 0.465cum machine mixed, machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation including cost of all materials, formwork, labour, HOM curing complete as per specifications. Specification No. KBS 4.1, 4.2 compelte with all lead and lift and as per specifications For CC Road | 217 | Cum | 4700 |  |  |  |  | 1019900
2 | 55 | Constructing cement concrete for pavements using Grade concrete M30 over a prepared base, with OPC coarse aggregate at 0.69 cum, fine aggregates at 0.46 cum, Coarse and fine aggregate conforming to IS:383-2016, with Superplastizer at 3 lts conforming to IS 9103-2008. mixed in a concrete mixer of not less than 0.6 cum capacity and appropriate weigh batcher as per approved mix design, laid in approved fixed side form work (steel channel, laying and fixing of 125 micron thick polythene film, wedges, steel plates including levelling the form work as per drawing) & Spreading the concrete with shovels, rackers compacted using needle, screed and plate vibrator and finished with floaters in a continuous operation including provision of contraction, expansion, construction and longitudinal joints, including groove cutting charges, joint filler, separation membrane of impermiable plastic sheet of 125 micron, sealant primer, joint sealant, admixtures as approved, curing compound, finishing to lines and grades, textured with texturing machine and curing including cost of all materials, labour, hire charges of machineries, all lead & lift charges etc., complete as per specifications. do- with OPC at 360 kg/cum and coarse aggregate 0.69cum, fine aggregate 0.46cum. Excluding cost of steel complete as per specification and as directed | 434 | Cum | 6400 |  |  |  |  | 2777600
2 | 56 | Conducting ground penetrating RADAR SURVEY in a corridor of 4-6 meter width to detect burred utilities like pipes, cables etc. in such corridor. Marking of the detected utilities on the map of corridor with information of locations and depth to the top of various utilities detected. Work to be conducted using 500 Mhz and 300 Mhz antenna or laterst equipment for the best possible resolution and penetration etc. complete with all lead and lift and as per the direction of the Engineer for the following | [7 empty] | 0
3 | a | Along the road crossings without dividers and upto 30 M width | 2 | nos | 40000 |  |  |  |  | 80000
2 | 57 | Conducting Seismic Refraction survey to determine stratigraphy along proposed route i.e, soil, seathered rock, rock interfaces. Detection of faults, fractures, shear zones etc. in the investigated area. Geophone spacing 5M or as requried, test to be conducted using 24 channel signal enhancement type seismograph or as required, 5M Geophone Spacing or as required with all lead and lift and as directed | 60 | m | 500 |  |  |  |  | 30000
2 | 58 | Installation of product pipe by Auger Boring method including making entry and exit pits, all related civil works like excavation, shoring, strutting, dewatering etc, shielded excavation through auger boring process, lowering of pipe segments in the jacking pit, laying and jointing of product pipeline through jacking process from jacking pit including the cost of RCC NP3 S&S or as required pipes including dewatering and other works required for commissioning of the works in all types of soil including rock complete with all lead and lift as per specifications and as directed complete for the following | [7 empty] | 0
3 | a | 400 mm dia | 30 | Rmt | 26000 |  |  |  |  | 780000
3 | b | 500 mm dia | 30 | Rmt | 35000 |  |  |  |  | 1050000
|  | Grand Total to be Carry forwarded to schedule No. SEWER 1 of Grand Summary for CP 25 | [7 empty] | 112729571

## Schedule 2
SEWER 2: Bill of Quantities for Sub-mains and Trunk Lines of Ananthapura and Yelahankakere Villages of Bytrayanapura Zone-2
Level | Item No. | Description | Quantity | Units | Rate (INR) | Duties | Ex.Work | Local Transport | GST | Amount (INR)
2 | 1 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN ALL KINDS OF SOIL MIXED WITH BOULDERS of 30cm size upto and exclusive of disintegrated rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following
3 | a | IN ALL KINDS OF SOIL MIXED WITH BOULDERS
4 | i | 0 to 2 Mts. Depth | 13622 | Cum | 265 |  |  |  |  | 3609830
4 | ii | 2 to 4 Mts. Depth | 8501 | Cum | 305 |  |  |  |  | 2592805
4 | iii | 4 to 6 Mts. Depth | 1608 | Cum | 340 |  |  |  |  | 546720
4 | iv | 6 to 8 Mts. Depth | 109 | Cum | 400 |  |  |  |  | 43600
3 | b | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN DISINTEGRATED ROCK, SOFT ROCK, SOFT SHALE AND MEDIUM HARD ROCK COMPRISING OF LIME STONE, SAND STONE, HARD SHALE, SCHIEST, FISSURED ROCK including all types of laterite without resorting to blasting or as directed including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 3406 | Cum | 345 |  |  |  |  | 1175070
4 | ii | 2 to 4 Mts. Depth | 2126 | Cum | 392 |  |  |  |  | 833392
4 | iii | 4 to 6 Mts. Depth | 403 | Cum | 442 |  |  |  |  | 178126
4 | iv | 6 to 8 Mts. Depth | 28 | Cum | 493 |  |  |  |  | 13804
3 | c | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. in hard rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 1874 | Cum | 1263 |  |  |  |  | 2366862
4 | ii | 2 to 4 Mts. Depth | 1170 | Cum | 1700 |  |  |  |  | 1989000
4 | iii | 4 to 6 Mts. Depth | 222 | Cum | 2300 |  |  |  |  | 510600
4 | iv | 6 to 8 Mts. Depth | 15 | Cum | 2400 |  |  |  |  | 36000
3 | d | Excavation of hard rock by using Machinery like Generator, Hitachi, Breaker, Compressor, Diamond Rope with MS rods or as directed etc. with all lead and lift complete as per specifications and drawings and as directed including utility restoration, clearing and grubbing with all lead and lift as per drawings & specification and as directed | 1193 | Cum | 4462 |  |  |  |  | 5323166
2 | 2 | Providing, erecting and removing casurina pole three tier BARRICADING using poles of 7.5 to 10 cms dia or as required and minimum 1.5M height above ground fixed vertically at intervals of 2.0 to 2.5 M centre to centre or as required and horizontally at 0.5M above ground level or as required, including fixing poles in ground for a maximum depth of 0.3M and tied with coir rope firmly including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed | 7083 | Rmt | 44 |  |  |  |  | 311652
2 | 3 | Refilling of available earth around pipelines, in layers not exceeding 20 cms in depth, compacting each deposited layer by ramming after watering all lead and lift including cost of all labour including consolidation by mechanical or manual means as approved by Engineer, when earth is at suitable moisture content with desired field density upto 95% maximum dry density (modified heavy proctor test) for restoration of roads without settlement including HOM of machineries, complete. (The contractor shall take care while consolidating the earth, so that, pipes laid are not damaged due to mechanical compaction and shall restore the damaged pipes at his own cost, in case of damage) with all lead and lift and as directed complete | 25704 | Cum | 110 |  |  |  |  | 2827440
2 | 4 | Extra charges for excavation in all classifications in watery situations or foul conditions as under towards dewatering with all recuperation rates with all lead including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed until completion of the works for the following - 0 to 2 Mtr. Depth | 7382 | Cum | 52 |  |  |  |  | 383864
3 | a | 2 to 4 m depth | 2507 | Cum | 78 |  |  |  |  | 195546
3 | b | 4 to 6 m depth | 438 | Cum | 104 |  |  |  |  | 45552
3 | c | 6 to 8 m depth | 29 | Cum | 130 |  |  |  |  | 3770
2 | 5 | Cutting road surface for pipeline trenches as per specifications and as directed and including disposing off the unserviceble excavated stuff as directed including barricading, danger lighting etc, in the following classifications with all lead and lift and as directed for the following | [7 empty] | 0
3 | a | Cutting asphalt road | 1431 | Cum | 759 |  |  |  |  | 1086129
3 | b | Cutting CC Road | 359 | Cum | 1150 |  |  |  |  | 412850
2 | 6 | Providing and laying Plain Cement Concrete 1:2:4 of specified grade for foundations (screed layer) with 20 mm and down size of approved gradation hard broken granite, trap basalt or with any other approved hard aggregate including cost and conveyance of all materials, lead and lifts, plywood / steel form works, machine mixing, laying, tamping, curing etc. complete and as per specification and as directed for the following | [7 empty] | 0
3 | a | For Bedding of Sewer Pipes and other works | 281 | Cum | 4000 |  |  |  |  | 1124000
2 | 7 | Providing and laying plain/reinforced cement concrete for side drains using M20 nominal mix concrete with OPC at minimum 300 kgs with 20 mm and down size granite metal coarse aggregates at 0.69 cum and fine aggregates at 0.43 cum as per desing mix, machine mixed, well compacted for walls and bottom including centering, shuttering, cost of materials, HOM of machinery, curing etc., complete including cost of admixuture excluding cost of steel as per MORTH specification No. 1500, 1700, 2200. including cost of materials, labour, HOM complete as per specifications for raft and walls of SWD works or other works as directed | 68 | Cum | 6189 |  |  |  |  | 420852
2 | 8 | Providing and laying cement concrete 1:1.5:3 proportion for RCC works of raft, footings, encasing of pipes or other works as directed with 20 mm and down size of approved gradation hard broken granite, trap, basalt or with any other approved hard aggregate including machine mixing, cost and conveyance of all materials with all lead and lifts including plywood / steel form work, machine mixing, laying in layers of 15 cm, compacted, curing, smooth finishing etc. complete with all lead and lift and as directed (excluding the cost of reinforcement). For Encasement | 557 | Cum | 5025 |  |  |  |  | 2798925
2 | 9 | KSRB 4-9.2: Providing TMT Fe 500 steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications with all lead and lift complete. Specification No. KBS 4.6.3 | 36825 | Kgs | 49 |  |  |  |  | 1804425
2 | 10 | KSRRB M700-4. Providing and Laying Boulder Apron in Crates of Synthetic Geogrids:- Providing, preparing and laying of geogrids crated apron of required thickness including excavation and backfilling with geogrids having characteristics as per clause 700.4.2, joining sides with connectors/ring staples or as required, top corners to be tie tensioned or as required, placing of suitable cross interval ties in layers of 300 mm or as required connecting opposite side with lateral braces and tied with polymer braids to avoid bulging, constructed as per clause 700.4.3. filled with stone as per specification for providing aroud the sewer pipe for pipe bedding/anchoring and as per specifications. For Pipe bedding in water logged area | 100 | Cum | 3700 |  |  |  |  | 370000
2 | 11 (a) | Providing Precast anti floatation blocks of RCC M20 grade concrete including casting at yard, including cost of reinforcement, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site, including providing and fixing of anchor bolts during precasting including cost of erection of anti floatation block below the sewer pipe and fixing of the steel strips as per requirement (including cost of steel strip for fixing of minimum 32mm wide and minimum 8 mm thick) including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 20 | Cum | 5550 |  |  |  |  | 111000
2 | b | Providing, driving and anchoring minimum 8 mm diameter minimum HYSD FE 500 reinforcement including cost of bending, driving, sharpening the edge for driving including cost of material, labour and other materials required as per drawings and specifications and as directed by the Engineer for holding the pipe in uplift situations complete with all lead and lift as per specification and as directed | 167 | m | 45 |  |  |  |  | 7515
2 | c | Providing Pre cast anti floatation slabs of RCC M20 grade concrete including casting at yard, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site including cost of steel strip of minimum 32mm wide and minimum 8 mm thick including providing and fixing of lifting hooks anchor bolts during precasting and nuts including cost of erection of anti floatation slabs below the sewer pipe and fixing of the steel strips as required including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 42 | Sqm | 5550 |  |  |  |  | 233100
2 | 12 | Providing and removing shoring and strutting for protecting both sides of pipe line trenches,where ever required, including the cost of all required materials and labour, safety requirements, including maintaining the shoring until completion of works complete as per specification NO.KBS 2.5/2.13 (for both sides single measument will be taken) with all lead and lift and as per the direction of the engineer complete | 8748 | Sqm | 460 |  |  |  |  | 4024080
2 | 13 | MS Sheet Piling - Providing and installing sheet piling for both sides of the trench for following depths, with Mild Steel Sheets not less than 6.5mm thick, stronger knife edge, recessed spreader sockets, 3" single or double wall shields, to be designed by the contractor to withstand all types of soils, maximum depths of as per the approved design drawing, including labour charges for installing and removing the sheet piling at various reaches of sewer line construction, including loading, unloading, transporting to the suitable location etc., complete with all lead and lifts (Measurement shall be taken for one side only even though it is provided for both sides) and maintaining the sheet piling until completion of works complete Above 3m Depth | 2188 | Sqm | 675 |  |  |  |  | 1476900
2 | 14 | Supplying DOUBLE WALL CORRUGATED (External annular corrugated & smooth internal wall) (DWC) of class SN 8, S & S piping system in accordance with IS 16098 (Part-2) and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, including rubber rings conforming to IS 5382 and cuts of pipes wherever necessary including jointing with all labour, lead & lifts, complete and giving necessary hydraulic test to the required pressure as per ISS (contractor will make his own arrangements for procuring water for testing) etc. for the following | [7 empty] | 0
3 | a | Pipes of SN 8, 300 mm dia. | 986 | Rmt | 1750 |  |  |  |  | 1725500
3 | b | Pipes of SN 8, 400 mm dia. | 918 | Rmt | 2800 |  |  |  |  | 2570400
3 | c | Pipes of SN 8, 500 mm dia. | 239 | Rmt | 4800 |  |  |  |  | 1147200
3 | d | Pipes of SN 8, 600 mm dia. | 81 | Rmt | 8000 |  |  |  |  | 648000
3 | e | Pipes of SN 8,800 mm dia | 50 | Rmt | 10000 |  |  |  |  | 500000
2 | 15 | Supplying of following diameters S&S RCC SPUN / VIBRATED CAST PIPES (REINFORCED) of NP-3 class conforming to IS 458:1988 with latest amendments manufactured using sulphate resistant cement and conveying to worksite, rolling and lowering into trenches, laying true to line and level including loading and unloading at both destinations and jointing of pipes & specials including cost of specials including perfect linking of joints with jack to correct position including cost of jointing materials i.e., rubber rings confirming to IS : 5382 for S&S RCC pipes with all lead and lifts as directed and giving necessary hydraulic test as per ISS and testing & commissioning etc., complete. (Contractor will make his own arrangements for procuring water for testing) including cost of all materials, labour complete as per specification and as directed for the following | [7 empty] | 0
3 | a | 300 | 423 | Rmt | 2100 |  |  |  |  | 888300
3 | b | 400 | 394 | Rmt | 3250 |  |  |  |  | 1280500
3 | c | 500 | 2145 | Rmt | 4700 |  |  |  |  | 10081500
3 | d | 600 | 728 | Rmt | 5000 |  |  |  |  | 3640000
3 | e | 700 | 445 | Rmt | 5900 |  |  |  |  | 2625500
2 | 16 | Providing and laying testing and commissioning of Ductile iron pipes of class-K7 conforming to IS 8329:2000 with latest amendments, conveying to work site, rolling and lowering into trenches, laying true to line, level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, cutting of pipes wherever necessary, jointing with rubber gaskets, cleaning the socket and spigot end with soap solution, applying soft soap to the socket and spigot ends before insertion of rubber gaskets, jacking and fixing in perfect conditions etc. The cost to include soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS with all lead and lifts and cost of all jointing materials. (The contractor will make his own arrangements for water) the internal cement motor linning shall be with High Alumina Cement (HAC) internal cement mortal lining (CML) of DI pipes complete as per specification and as directed with all lead and lift complete for (For Major Storm Water Drain Crossing) for the following | [7 empty] | 0
3 | a | 300 mm dia | 70 | Rmt | 3200 |  |  |  |  | 224000
3 | b | 400 mm dia | 60 | Rmt | 4800 |  |  |  |  | 288000
3 | c | 500 mm dia | 100 | Rmt | 7000 |  |  |  |  | 700000
3 | d | 600 mm dia | 40 | Rmt | 9000 |  |  |  |  | 360000
3 | e | 700 mm dia | 30 | Rmt | 11000 |  |  |  |  | 330000
2 | 17 | Construction of RCC manhole chambers of RCC M 30 Grade approved type pre-cast RCC manhole chambers, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resitant cement, using RCC M 30 grade proportion with 20mm and downgraded jelly, well graded sand and reinforcement steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of house service connection, incoming and outgoing pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including excavation in all types of soil/rock, dewatering, refilling, sand bedding wherever required, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 4 | nos | 49000 |  |  |  |  | 196000
4 | ii | For every additional 0.1m upto 2m | 38 | nos | 4 |  |  |  |  | 152
4 | iii | 2mdepth | 17 | nos | 68000 |  |  |  |  | 1156000
4 | iv | For every additional 0.1m upto 3m | 31 | nos | 1900 |  |  |  |  | 58900
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 60 | nos | 73000 |  |  |  |  | 4380000
4 | ii | For every additional 0.1m upto 3m | 426 | nos | 2200 |  |  |  |  | 937200
4 | iii | 3m depth | 36 | nos | 98000 |  |  |  |  | 3528000
4 | iv | For every additional 0.1m upto 4m | 196 | nos | 2225 |  |  |  |  | 436100
4 | v | 4m depth | 41 | nos | 116000 |  |  |  |  | 4756000
4 | vi | For every additional 0.1m upto 5m | 181 | nos | 2250 |  |  |  |  | 407250
4 | vii | 5m depth | 7 | nos | 125000 |  |  |  |  | 875000
4 | viii | For every additional 0.1m upto 6m | 27 | nos | 2250 |  |  |  |  | 60750
3 | c | 1.8m Diameter manholes | [7 empty] | 0
4 | i | 6m depth | 1 | nos | 180000 |  |  |  |  | 180000
4 | ii | For every additional 0.1m upto 7m | 4 | nos | 2600 |  |  |  |  | 10400
4 | iii | 7m depth | 2 | nos | 225000 |  |  |  |  | 450000
4 | iv | For every additional 0.1m upto 8m | 6 | nos | 2800 |  |  |  |  | 16800
2 | 18 | Cast in Situ Manholes in Drain/Nallah Edge/Road: Construction of RCC manhole chambers of M30 Grade proportion, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resistant cement, using M30 grade RCC with 20mm and downgraded jelly, well graded sand and steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including sand bedding wherever required, including earthwork in all types of soil/rock, dewatering, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 6 | nos | 48000 |  |  |  |  | 288000
4 | ii | For every additional 0.1m upto 2m | 60 | nos | 1700 |  |  |  |  | 102000
4 | iii | 2mdepth | 7 | nos | 65000 |  |  |  |  | 455000
4 | iv | For every additional 0.1m upto 3m | 12 | nos | 1900 |  |  |  |  | 22800
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 25 | nos | 74000 |  |  |  |  | 1850000
4 | ii | For every additional 0.1m upto 3m | 179 | nos | 1900 |  |  |  |  | 340100
4 | iii | 3m depth | 12 | nos | 93000 |  |  |  |  | 1116000
4 | iv | For every additional 0.1m upto 4m | 38 | nos | 2400 |  |  |  |  | 91200
2 | 19 | Providing and fixing DROP ARRANGEMENT with following dia. HDPE grade PE-100 pipes, conforming to PN 6 as per IS 14333 with latest amendments, vertical drop pipe with MS fastenings at 300 mm C/C or suitable materaial as required, with suitable expander / reducer HDPE ‘T’ joint at top with incoming sewer with one end of Tee inside the manhole closed with end cap and 45 degree bend at the bottom with HDPE specials and encasing the pipe outside the manhole with cement concrete 1:2:4 proportion, 150 / 200 mm thick alround the HDPE pipe, including vibrating, compacting, necessary centering and form work, curing, testing etc. including cost and conveyance of all materials, labour with all lead and lifts etc. complete as per specification, drawings and as directed by the Engineer in charge etc. for the followng complete with all lead and lift | [7 empty] | 0
3 | a | For 300 mm dia. incoming sewer pipe. | 22 | Rmt | 8420 |  |  |  |  | 185240
3 | b | For 350 mm to 500 mm dia. incoming sewer pipe. | 56 | Rmt | 13140 |  |  |  |  | 735840
3 | c | For 600 mm to 750 mm dia. incoming sewer pipe. | 19 | Rmt | 26325 |  |  |  |  | 500175
2 | 20 | Dewatering the sewage or other drainage water by using minimum 5 HP pump for the diversion of storm / sewage including cost of machinery, piping upto disposal point, fuel, operator, HOM of machinery complete including diverting to the safe location as per specifications and as per the direction of the engineer with all lead and lift complete | 1040 | Hr | 185 |  |  |  |  | 192400
2 | 21 | Overpumping charges for pumping of sewage for pumping of sewage from u/s manhole to the d/s manholes or as directed including cost of machinery, piping as per site requirement, fuel, operator, HOM of machinery complete as per specifications and as per the direction of the engineer with all lead and lift | 1040 | Hr | 525 |  |  |  |  | 546000
2 | 22 | Providing sewer plugs of required sizes as per site requirement or plugging of manholes with sand / clay bags & other materials as required for the plugging/diversion of sewage from existing manholes including all required safety equipment, approvals, complete with all lead and lift and as directed | 65 | nos | 380 |  |  |  |  | 24700
2 | 23 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Dismantling Stone Masonry and Rubble stone Masonry in cement mortar as per the direction of the Engineer | 70 | Cum | 1000 |  |  |  |  | 70000
2 | 24 | Construction of dismatled size stone masonry with available stones including curing and mortar (in CM 1:6) including cost of all other required materials, required labour, machinery, curing complete with all lead and lift and as per specification and as directed | 20 | Cum | 3650 |  |  |  |  | 73000
2 | 25 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Reinforced Cement Concrete grade M20 and above as per the direction of the Engineer | 68 | Cum | 1000 |  |  |  |  | 68000
2 | 26 | KSRB 5-2.3: Providing and constructing granite/trap/basalt size stone masonry in Foundation or as required with cement mortar 1:6, stone hammered dressed in courses not less than 20cm high, bond stones at two m. apart in each course including cost of materials, labour, curing complete as per specifications. Specification No. KBS 5.1.13 complete with all lead and lift and as directed | 50 | Cum | 3650 |  |  |  |  | 182500
2 | 27 | Providing and filling in foundation/trench bottom with granite/ trap broken metal 100mm and down size with stone spalls/boulders to fill the voids, hand roller, ramming including cost of all material and labour with all lead and lifts, complete as per the specification in slushy soil for soling work complete as directed | 122 | Cum | 785 |  |  |  |  | 95770
2 | 28 | Disposing of excavated Earth of all types to a distance of upto average one side distance of 25 kilometers by vehicle including head load where ever required including loading, unloading to approved location with all lifts, labour, HOM of machinery etc. complete as per specification and as directed | 4099 | Cum | 440 |  |  |  |  | 1803560
2 | 29 (a) | Conducting the Level and Strip of Survey of alignment of Main Sewers of diameter 300mm and above, including all data required for generating GIS maps of sewer network, preparation and submission of plan & LS with ground level at 30m interval and junction points along the centre line of the alignment etc., showing the right of way, any permanent features, culverts including providing branch sewer pipeline catment survey & manhole details complete as per specifications and as directed by the Engineer in charge with all lead and lifts etc., complete for the following: for 300 mm dia | 1409 | Rmt | 18 |  |  |  |  | 25362
2 | b | Above 300 mm dia | 5000 | Rmt | 24.5 |  |  |  |  | 122500
2 | 30 | Providing and fixing 150mm dia Cast Iron pipe for ventilating shaft minimum 5m high with specials and cowl and with suitable grips in CC 1:2:4 pillar using 10mm to 20mm graded hard granite/trap/basalt or any other approved metal with 15cms thick cement concrete (1:2:4) around up to 1.22 mtrs above the GLR and with a foundation base of 90x90x90 cms plastered with 12 mm thick CMC 1:3 to all exposed faces and linking the shaft to the manholes by means of 15 cm dia GSW pipes and specials, jointing with tar dipped hemp 1:1½ CM caulking, curing with all lead and lifts etc., complete for all materials earth work excavation and refilling in all strata and disposal of surplus earth as directed with all lead and lifts etc., complete | 2 | nos | 21000 |  |  |  |  | 42000
2 | 31 | Providing gravel bedding for the pipe line trenches using approved granular material of size less than 25mm (murrum) including watering and consolidation by punners etc., complete with all lead and lifts, as per specification and as directed by the Engineer complete | 1579 | Cum | 480 |  |  |  |  | 757920
2 | 32 | Providing Bedding or Backfillling using approved stone dust/quarry dust of size not exceeding 5.6mm for the pipe line trenches including watering and consolidation to 95% proctor density etc., complete with all lead and lifts as per specification and as directed by the Engineer complete | 383 | Cum | 799 |  |  |  |  | 306017
2 | 33 | Provide murrum bedding for the pipeline trenches in black cotton and rock reaches or as per site requirement including watering and consolidation by punners etc. complete with all lead and lift and as directed complete | 192 | Cum | 209 |  |  |  |  | 40128
2 | 34 | KSRRB M200-14.1. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications. MORTH Specification No. 202 for Dismantling brick In cement mortar as as per the direction of the Engineer | 50 | Cum | 220 |  |  |  |  | 11000
2 | 35 | KSRB 6-2 : Providing and constructing burnt brick masonry with approved quality of non-modular bricks of standard size of class designation 5.0 Newton per sqmm (table moulded) with cement mortar 1:6 for basement and superstructure including cost of materials, labour charges, scaffolding, curing complete as per specifications. Specification No. KBS 6.2 complete with all lead and lift and as directed by the Engineer | 50 | Cum | 5820 |  |  |  |  | 291000
2 | 36 | Removing B.S. slabs of Drain and stacking with all lead and lifts as directed by the Engineer | 250 | Sqm | 54.5 |  |  |  |  | 13625
2 | 37 | Refixing of the available stone slabs of drains including other required materials and pointing in C.M. (1:3) with all lead and lifts complete and as directed by the Engineer complete | 250 | Sqm | 67 |  |  |  |  | 16750
2 | 38 | Providing granite slabs of 7.50 cms thick of selected quality roughly dressed and fixed in cement mortar (1:6), including pointing, curing etc complete with all lead and lifts as per specification and as directed by the Engineer . | 200 | Sqm | 548 |  |  |  |  | 109600
2 | 39 | Supplying to work spot rolling, lowering and placing in position RCC perforated rings in the already excavated pit including loading and unloading at both the destinations with all lead and lift etc., complete for soak pits including removal/dismantling of existing soak pits including disposal of unserviseble materials with all lead and lift complete | 10 | Each | 6290 |  |  |  |  | 62900
2 | 40 | Making bore in manholes without damaging the existing manholes, fixing the pipe of any diameter in line and level with CC 1:2:4, plastering the outer and inner surface in CM 1:3 including curing etc. using Sulphate Resistant Cement including disposal of debris. The cost includes the cost of materials, labour charges, lead and lifts etc. complete as per specifications and as directed by the Engineer. | 33 | nos | 180 |  |  |  |  | 5940
2 | 41 | Removing manhole cover and frame carefully and refixing the same in CC 1:2:4 band and finishing as per drawings complete with all lead and lift including disposal of the unserviceble materials complete as directed | 33 | nos | 2000 |  |  |  |  | 66000
2 | 42 | Removing of kerb stones carefully and resetting, rifixing of the kerb stones after completion of works and as directed complete with all lead and lift as per the specification | 2184 | m | 56 |  |  |  |  | 122304
2 | 43 (a) | KSRB 14.6 : Providing and laying with new heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications Specification No. KBS with all lead and lift and as directed complete | 219 | Sqm | 850 |  |  |  |  | 186150
2 | b | KSRB 14.6 : Providing and laying with available heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications. Specification No. KBS with all lead and lift and as per specification | 1966 | Sqm | 450 |  |  |  |  | 884700
2 | 44 | Diversion of water course by providing Coffer dams or bunds or islands as may be necessary for laying of sewer network including bailing out or pumping water during excavation and until completion of works etc., including cost of materials, labour, HOM complete as per specifications with all lead and lift complete as per specificaiton and as directed | 6190 | Cum | 300 |  |  |  |  | 1857000
2 | 45 | Cutting of trees of the following girths, including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in depression/pits etc. including labour charges, all lead and lifts etc. all as per specifications and instructions of the Engineer in charge. MOST specification 201 for the following | [7 empty] | 0
3 | a | For trees of 300 mm to 600 mm girth | 15 | nos | 77 |  |  |  |  | 1155
3 | b | For trees of 600 mm to 1200 mm girth | 15 | nos | 98 |  |  |  |  | 1470
2 | 46 | KSRB M 300-54, Construction of embankment with approved new material with all lead and lift graded and compacted to meet requirement of table 300-2 complete as per Specification which includes watering & compaction by virbratory roller/ramper/plate vibrator. MOSRTH Specification No.305 complete | 1754 | Cum | 185 |  |  |  |  | 324490
2 | 47 | Provide bedding using approved stone dust / quarry dust of size not exceeding 5.6 mm for the pipe lines trenches including watering and consolidation to 95% proctor density etc. complete with all lead and lifts as per specifications and as directed by the Engineer complete | 1754 | Cum | 805 |  |  |  |  | 1411970
2 | 48 | Construction of granular sub-base Grading-V as Sub-base and drainage layer by providing coarse graded crushed stone aggregates of granite/trap/basalt material, mixing by mix in place method by rotavator at OMC, spreading in uniform layers with motor grader on prepared surface and compacting with vibratory power roller to achieve the 98 % proctor density, complete as per specifications. Clause 401 of MORTH V Revision For Grade II Material or as required and directed complete with all lead and lift | 1754 | Cum | 1450 |  |  |  |  | 2543300
2 | 49 | KSRRB M400-14.1. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt of specific sizes to water bound macadam specifications including spreading in uniform thickness, hand packing, rolling with 3-wheeled steel/vibratory roller 8-10 tonnes in stages to proper grade and camber, applying and brooming requisite type of screening/binding materials to fill up the interstices of coarse aggregates, watering and compacting to the required density complete as per Specification. A. By manual means. MORTH Specification No. 404 Type B 11.2mm for grading III complete with all lead and lift complete as per specification and as directed | 176 | Cum | 1625 |  |  |  |  | 286000
2 | 50 | KSRRB M400-17. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt to wet mix macadam specifications including pre mixing the material with water at OMC in mechanical mix plant carriage of mixed materials by tipper to site, laying in uniform layers with paver in sub-base/base course on well prepared surface and compacting with vibratory roller to achieve the desired density complete as per specifications. MORTH Specification No. 406 with all lead and lift complete as per specification and as directed | 702 | Cum | 1800 |  |  |  |  | 1263600
2 | 51 | KSRRB M500-6. Providing and applying primer coat with S.S. bitumen emulsion on prepared surface of granular base such as WMM including cleaning of road surface and spraying primer at the rate of 0.60 kg / sqm using mechanical means complete as per specifications. Clause 502 of MORTH V revision with all lead and lift complete | 4676 | Sqm | 25 |  |  |  |  | 116900
2 | 52 | KSRRB 500-7. Providing and applying tack coat using 80/100 grade bitumen (VG10) on the prepared black topped surfaces at 2.5 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 4676 | Sqm | 13 |  |  |  |  | 60788
2 | 53 | KSRRB 500-9. Providing and applying tack coat using 80/100 grade bitumen (VG10) on granular base such as WBM surfaces hot bitumen primed at 4 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 1170 | Sqm | 20 |  |  |  |  | 23400
2 | 54 | KSRRB 500-11. Providing and laying bituminous macadam on prepared surface with crushed coarse aggregates as per design mix formula for base / binding course including loading of aggregates with F.E. loader, hot mixing of stone aggregates and bitumen in hot mix plant, transporting the mixed material in tipper to paver and laying mixed materials with paver finisher to the required level and grade, rolling by smooth wheeled, vibratory & tandem rollers to achieve the desired density, but excluding cost of primer / tack coat & including lead, lift and cost of all materials, labour, HOM complete as per specifications. Clause 504 of MORTH V revision do - using 40/60 TPH capacity H.M.P. with Mechanical paver Gr-II (50 mm to 75 mm or as directed) with 3.4% VG-30 Bitumen complete with all lead and lift and as directed | 235 | Cum | 6000 |  |  |  |  | 1410000
2 | 55 | KSRB M500-18, Providing and laying semi dense bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause no 508 complete in all respects as per specification with all lead and lift do using 40/60 TPH capacity HMP with Mechanical Paver Gr-II (25 mm to 30 mm or as directed ) with 5% VG-30 Bitumen compelte with all lead and lift and as per specifications | 118 | Cum | 7200 |  |  |  |  | 849600
2 | 56 | KSRRB M500-19. Providing and laying bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler, transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction in all respects complete as per specifications. Clause 507 of MORTH V revision do - using40/60 TPH capacity H.M.P. with Mechanical Paver Gr-II (30 mm to 40 mm or as directed) with 5.4% VG-30 Bitumen compelte with all lead and lift and as per specifications | 60 | Cum | 8000 |  |  |  |  | 480000
2 | 57 | KSRB 4-1.2 : Providing and laying in position plain cement concrete of Mix 1:3:6 with OPC @ minimum 220kgs, with 40mm and down size graded granite metal coarse aggregates @0.892cum and fine aggregates @ 0.465cum machine mixed, machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation including cost of all materials, formwork, labour, HOM curing complete as per specifications. Specification No. KBS 4.1, 4.2 compelte with all lead and lift and as per specifications For CC Road | 196 | Cum | 4700 |  |  |  |  | 921200
2 | 58 | Constructing cement concrete for pavements using Grade concrete M30 over a prepared base, with OPC coarse aggregate at 0.69 cum, fine aggregates at 0.46 cum, Coarse and fine aggregate conforming to IS:383-2016, with Superplastizer at 3 lts conforming to IS 9103-2008. mixed in a concrete mixer of not less than 0.6 cum capacity and appropriate weigh batcher as per approved mix design, laid in approved fixed side form work (steel channel, laying and fixing of 125 micron thick polythene film, wedges, steel plates including levelling the form work as per drawing) & Spreading the concrete with shovels, rackers compacted using needle, screed and plate vibrator and finished with floaters in a continuous operation including provision of contraction, expansion, construction and longitudinal joints, including groove cutting charges, joint filler, separation membrane of impermiable plastic sheet of 125 micron, sealant primer, joint sealant, admixtures as approved, curing compound, finishing to lines and grades, textured with texturing machine and curing including cost of all materials, labour, hire charges of machineries, all lead & lift charges etc., complete as per specifications. do- with OPC at 360 kg/cum and coarse aggregate 0.69cum, fine aggregate 0.46cum. Excluding cost of steel complete as per specification and as directed | 390 | Cum | 6300 |  |  |  |  | 2457000
2 | 59 | Conducting ground penetrating RADAR SURVEY in a corridor of 4-6 meter width to detect burred utilities like pipes, cables etc. in such corridor. Marking of the detected utilities on the map of corridor with information of locations and depth to the top of various utilities detected. Work to be conducted using 500 Mhz and 300 Mhz antenna or laterst equipment for the best possible resolution and penetration etc. complete with all lead and lift and as per the direction of the Engineer for the following | [7 empty] | 0
3 | a | Along the road crossings with dividers and upto 50 M width. | 1 | nos | 69000 |  |  |  |  | 69000
2 | 60 | Conducting Seismic Refraction survey to determine stratigraphy along proposed route i.e, soil, seathered rock, rock interfaces. Detection of faults, fractures, shear zones etc. in the investigated area. Geophone spacing 5M or as requried, test to be conducted using 24 channel signal enhancement type seismograph or as required, 5M Geophone Spacing or as required with all lead and lift and as directed | 50 | m | 500 |  |  |  |  | 25000
2 | 61 | Installation of product pipe by Micro Tunneling method including concrete structural shaft of sheet piles/RCC retaining walls/well sinking/secant piling as per respective site requirements all inclusive as per IndSTT: 102-2018: Code of Practice for Micro Tunneling & Pipe Jacking Suiting Indian Conditions including cost of RCC NP4 pipe complete including dewatering and other works required for commissioning of the works with all lead and lift as per specifications and as directed complete for the following For 1200 mm Dia | [7 empty] | 0
3 | a | All type of soil (Except mixed strata & rocks) | 20 | Rmt | 90000 |  |  |  |  | 1800000
3 | b | Mixed Strata | 20 | Rmt | 98000 |  |  |  |  | 1960000
3 | c | Rocks | 10 | Rmt | 160000 |  |  |  |  | 1600000
|  | Grand Total to be Carry forwarded to schedule No. SEWER 2 of Grand Summary for CP 25 | [7 empty] | 112582081

## Schedule 3
SEWER 3: Bill of Quantities for Sub-mains and Trunk Lines of Bellahalli -Thirumanahalli and Kattigenahalli Villages of Bytrayanapura Zone-3
Level | Item No. | Description | Quantity | Units | Rate (INR) | Duties | Ex.Work | Local Transport | GST | Amount (INR)
2 | 1 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN ALL KINDS OF SOIL MIXED WITH BOULDERS of 30cm size upto and exclusive of disintegrated rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following
3 | a | IN ALL KINDS OF SOIL MIXED WITH BOULDERS
4 | i | 0 to 2 Mts. Depth | 16886 | Cum | 265 |  |  |  |  | 4474790
4 | ii | 2 to 4 Mts. Depth | 11540 | Cum | 305 |  |  |  |  | 3519700
4 | iii | 4 to 6 Mts. Depth | 2879 | Cum | 340 |  |  |  |  | 978860
4 | iv | 6 to 8 Mts. Depth | 327 | Cum | 400 |  |  |  |  | 130800
3 | b | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN DISINTEGRATED ROCK, SOFT ROCK, SOFT SHALE AND MEDIUM HARD ROCK COMPRISING OF LIME STONE, SAND STONE, HARD SHALE, SCHIEST, FISSURED ROCK including all types of laterite without resorting to blasting or as directed including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 4222 | Cum | 345 |  |  |  |  | 1456590
4 | ii | 2 to 4 Mts. Depth | 2885 | Cum | 392 |  |  |  |  | 1130920
4 | iii | 4 to 6 Mts. Depth | 720 | Cum | 442 |  |  |  |  | 318240
4 | iv | 6 to 8 Mts. Depth | 82 | Cum | 493 |  |  |  |  | 40426
3 | c | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. in hard rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 2323 | Cum | 1250 |  |  |  |  | 2903750
4 | ii | 2 to 4 Mts. Depth | 1587 | Cum | 1600 |  |  |  |  | 2539200
4 | iii | 4 to 6 Mts. Depth | 396 | Cum | 2100 |  |  |  |  | 831600
4 | iv | 6 to 8 Mts. Depth | 45 | Cum | 2400 |  |  |  |  | 108000
3 | d | Excavation of hard rock by using Machinery like Generator, Hitachi, Breaker, Compressor, Diamond Rope with MS rods or as directed etc. with all lead and lift complete as per specifications and drawings and as directed including utility restoration, clearing and grubbing with all lead and lift as per drawings & specification and as directed | 1583 | Cum | 4400 |  |  |  |  | 6965200
2 | 2 | Providing, erecting and removing casurina pole three tier BARRICADING using poles of 7.5 to 10 cms dia or as required and minimum 1.5M height above ground fixed vertically at intervals of 2.0 to 2.5 M centre to centre or as required and horizontally at 0.5M above ground level or as required, including fixing poles in ground for a maximum depth of 0.3M and tied with coir rope firmly including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed | 8292 | Rmt | 44 |  |  |  |  | 364848
2 | 3 | Refilling of available earth around pipelines, in layers not exceeding 20 cms in depth, compacting each deposited layer by ramming after watering all lead and lift including cost of all labour including consolidation by mechanical or manual means as approved by Engineer, when earth is at suitable moisture content with desired field density upto 95% maximum dry density (modified heavy proctor test) for restoration of roads without settlement including HOM of machineries, complete. (The contractor shall take care while consolidating the earth, so that, pipes laid are not damaged due to mechanical compaction and shall restore the damaged pipes at his own cost, in case of damage) with all lead and lift and as directed complete | 33960 | Cum | 110 |  |  |  |  | 3735600
2 | 4 | Extra charges for excavation in all classifications in watery situations or foul conditions as under towards dewatering with all recuperation rates with all lead including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed until completion of the works for the following - 0 to 2 Mtr. Depth | 11155 | Cum | 52 |  |  |  |  | 580060
2 | a | 2 to 4 m depth | 5132 | Cum | 78 |  |  |  |  | 400296
2 | b | 4 to 6 m depth | 1324 | Cum | 104 |  |  |  |  | 137696
2 | c | 6 to 8 m depth | 151 | Cum | 130 |  |  |  |  | 19630
2 | 5 | Cutting road surface for pipeline trenches as per specifications and as directed and including disposing off the unserviceble excavated stuff as directed including barricading, danger lighting etc, in the following classifications with all lead and lift and as directed for the following | [7 empty] | 0
3 | a | Cutting asphalt road | 1627 | Cum | 750 |  |  |  |  | 1220250
3 | b | Cutting CC Road | 408 | Cum | 1150 |  |  |  |  | 469200
2 | 6 | Providing and laying Plain Cement Concrete 1:2:4 of specified grade for foundations (screed layer) with 20 mm and down size of approved gradation hard broken granite, trap basalt or with any other approved hard aggregate including cost and conveyance of all materials, lead and lifts, plywood / steel form works, machine mixing, laying, tamping, curing etc. complete and as per specification and as directed for the following | [7 empty] | 0
3 | a | For Bedding of Sewer Pipes and other works | 359 | Cum | 4000 |  |  |  |  | 1436000
2 | 7 | Providing and laying plain/reinforced cement concrete for side drains using M20 nominal mix concrete with OPC at minimum 300 kgs with 20 mm and down size granite metal coarse aggregates at 0.69 cum and fine aggregates at 0.43 cum as per desing mix, machine mixed, well compacted for walls and bottom including centering, shuttering, cost of materials, HOM of machinery, curing etc.,complete including cost of admixuture excluding cost of steel as per MORTH specification No. 1500, 1700, 2200. including cost of materials, labour, HOM complete as per specifications for raft and walls of SWD works or other works as directed | 97 | Cum | 6189 |  |  |  |  | 600333
2 | 8 | Providing and laying cement concrete 1:1.5:3 proportion for RCC works of raft, footings, encasing of pipes or other works as directed with 20 mm and down size of approved gradation hard broken granite, trap, basalt or with any other approved hard aggregate including machine mixing, cost and conveyance of all materials with all lead and lifts including plywood / steel form work, machine mixing, laying in layers of 15 cm, compacted, curing, smooth finishing etc. complete with all lead and lift and as directed (excluding the cost of reinforcement). For Encasement | 1033 | Cum | 5050 |  |  |  |  | 5216650
2 | 9 | KSRB 4-9.2: Providing TMT Fe 500 steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications with all lead and lift complete. Specification No. KBS 4.6.3 | 52525 | Kgs | 49 |  |  |  |  | 2573725
2 | 10 | KSRRB M700-4. Providing and Laying Boulder Apron in Crates of Synthetic Geogrids:- Providing, preparing and laying of geogrids crated apron of required thickness including excavation and backfilling with geogrids having characteristics as per clause 700.4.2, joining sides with connectors/ring staples or as required, top corners to be tie tensioned or as required, placing of suitable cross interval ties in layers of 300 mm or as required connecting opposite side with lateral braces and tied with polymer braids to avoid bulging, constructed as per clause 700.4.3. filled with stone as per specification for providing aroud the sewer pipe for pipe bedding/anchoring and as per specifications. For Pipe bedding in water logged area | 100 | Cum | 3700 |  |  |  |  | 370000
2 | 11 (a) | Providing Precast anti floatation blocks of RCC M20 grade concrete including casting at yard, including cost of reinforcement, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site, including providing and fixing of anchor bolts during precasting including cost of erection of anti floatation block below the sewer pipe and fixing of the steel strips as per requirement (including cost of steel strip for fixing of minimum 32mm wide and minimum 8 mm thick) including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 20 | Cum | 5550 |  |  |  |  | 111000
2 | b | Providing, driving and anchoring minimum 8 mm diameter minimum HYSD FE 500 reinforcement including cost of bending, driving, sharpening the edge for driving including cost of material, labour and other materials required as per drawings and specifications and as directed by the Engineer for holding the pipe in uplift situations complete with all lead and lift as per specification and as directed | 31 | m | 45 |  |  |  |  | 1395
2 | c | Providing Pre cast anti floatation slabs of RCC M20 grade concrete including casting at yard, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site including cost of steel strip of minimum 32mm wide and minimum 8 mm thick including providing and fixing of lifting hooks anchor bolts during precasting and nuts including cost of erection of anti floatation slabs below the sewer pipe and fixing of the steel strips as required including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 11 | Sqm | 5550 |  |  |  |  | 61050
2 | 12 | Providing and removing shoring and strutting for protecting both sides of pipe line trenches,where ever required, including the cost of all required materials and labour, safety requirements, including maintaining the shoring until completion of works complete as per specification NO.KBS 2.5/2.13 (for both sides single measument will be taken) with all lead and lift and as per the direction of the engineer complete | 11147 | Sqm | 455 |  |  |  |  | 5071885
2 | 13 | MS Sheet Piling - Providing and installing sheet piling for both sides of the trench for following depths, with Mild Steel Sheets not less than 6.5mm thick, stronger knife edge, recessed spreader sockets, 3" single or double wall shields, to be designed by the contractor to withstand all types of soils, maximum depths of as per the approved design drawing, including labour charges for installing and removing the sheet piling at various reaches of sewer line construction, including loading, unloading, transporting to the suitable location etc., complete with all lead and lifts (Measurement shall be taken for one side only even though it is provided for both sides) and maintaining the sheet piling until completion of works complete Above 3m Depth | 2788 | Sqm | 665 |  |  |  |  | 1854020
2 | 14 | Supplying DOUBLE WALL CORRUGATED (External annular corrugated & smooth internal wall) (DWC) of class SN 8, S & S piping system in accordance with IS 16098 (Part-2) and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, including rubber rings conforming to IS 5382 and cuts of pipes wherever necessary including jointing with all labour, lead & lifts, complete and giving necessary hydraulic test to the required pressure as per ISS (contractor will make his own arrangements for procuring water for testing) etc. for the following | [7 empty] | 0
3 | a | Pipes of SN 8, 300 mm dia. | 1160 | Rmt | 1750 |  |  |  |  | 2030000
3 | b | Pipes of SN 8, 400 mm dia. | 566 | Rmt | 2800 |  |  |  |  | 1584800
3 | c | Pipes of SN 8, 500 mm dia. | 61 | Rmt | 4800 |  |  |  |  | 292800
2 | 15 | Supplying of following diameters S&S RCC SPUN / VIBRATED CAST PIPES (REINFORCED) of NP-3 class conforming to IS 458:1988 with latest amendments manufactured using sulphate resistant cement and conveying to worksite, rolling and lowering into trenches, laying true to line and level including loading and unloading at both destinations and jointing of pipes & specials including cost of specials including perfect linking of joints with jack to correct position including cost of jointing materials i.e., rubber rings confirming to IS : 5382 for S&S RCC pipes with all lead and lifts as directed and giving necessary hydraulic test as per ISS and testing & commissioning etc., complete. (Contractor will make his own arrangements for procuring water for testing) including cost of all materials, labour complete as per specification and as directed for the following | [7 empty] | 0
3 | a | 300 | 497 | Rmt | 2200 |  |  |  |  | 1093400
3 | b | 400 | 243 | Rmt | 3350 |  |  |  |  | 814050
3 | c | 500 | 549 | Rmt | 4700 |  |  |  |  | 2580300
3 | d | 600 | 346 | Rmt | 5000 |  |  |  |  | 1730000
3 | e | 700 | 3695 | Rmt | 5900 |  |  |  |  | 21800500
2 | 16 | Providing and laying testing and commissioning of Ductile iron pipes of class-K7 conforming to IS 8329:2000 with latest amendments, conveying to work site, rolling and lowering into trenches, laying true to line, level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, cutting of pipes wherever necessary, jointing with rubber gaskets, cleaning the socket and spigot end with soap solution, applying soft soap to the socket and spigot ends before insertion of rubber gaskets, jacking and fixing in perfect conditions etc. The cost to include soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS with all lead and lifts and cost of all jointing materials. (The contractor will make his own arrangements for water) the internal cement motor linning shall be with High Alumina Cement (HAC) internal cement mortal lining (CML) of DI pipes complete as per specification and as directed with all lead and lift complete for (For Major Storm Water Drain Crossing) for the following | [7 empty] | 0
3 | a | 300 mm dia | 80 | Rmt | 3200 |  |  |  |  | 256000
3 | b | 400 mm dia | 40 | Rmt | 4800 |  |  |  |  | 192000
3 | c | 500 mm dia | 30 | Rmt | 6600 |  |  |  |  | 198000
3 | d | 600 mm dia | 30 | Rmt | 9000 |  |  |  |  | 270000
3 | e | 700 mm dia | 60 | Rmt | 11000 |  |  |  |  | 660000
2 | 17 | Construction of RCC manhole chambers of RCC M 30 Grade approved type pre-cast RCC manhole chambers, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resitant cement, using RCC M 30 grade proportion with 20mm and downgraded jelly, well graded sand and reinforcement steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of house service connection, incoming and outgoing pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including excavation in all types of soil/rock, dewatering, refilling, sand bedding wherever required, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 22 | nos | 49000 |  |  |  |  | 1078000
4 | ii | For every additional 0.1m upto 2m | 207 | nos | 1800 |  |  |  |  | 372600
4 | iii | 2mdepth | 35 | nos | 68000 |  |  |  |  | 2380000
4 | iv | For every additional 0.1m upto 3m | 59 | nos | 1900 |  |  |  |  | 112100
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 58 | nos | 74000 |  |  |  |  | 4292000
4 | ii | For every additional 0.1m upto 3m | 387 | nos | 2200 |  |  |  |  | 851400
4 | iii | 3m depth | 29 | nos | 98000 |  |  |  |  | 2842000
4 | iv | For every additional 0.1m upto 4m | 141 | nos | 2225 |  |  |  |  | 313725
4 | v | 4m depth | 36 | nos | 116000 |  |  |  |  | 4176000
4 | vi | For every additional 0.1m upto 5m | 185 | nos | 2250 |  |  |  |  | 416250
4 | vii | 5m depth | 10 | nos | 125000 |  |  |  |  | 1250000
4 | viii | For every additional 0.1m upto 6m | 27 | nos | 2250 |  |  |  |  | 60750
3 | c | 1.8m Diameter manholes | [7 empty] | 0
4 | i | 6m depth | 4 | nos | 180000 |  |  |  |  | 720000
4 | ii | For every additional 0.1m upto 7m | 18 | nos | 2600 |  |  |  |  | 46800
4 | iii | 7m depth | 3 | nos | 220000 |  |  |  |  | 660000
4 | iv | For every additional 0.1m upto 8m | 6 | nos | 2800 |  |  |  |  | 16800
2 | 18 | Cast in Situ Manholes in Drain/Nallah Edge/Road: Construction of RCC manhole chambers of M30 Grade proportion, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resistant cement, using M30 grade RCC with 20mm and downgraded jelly, well graded sand and steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including sand bedding wherever required, including earthwork in all types of soil/rock, dewatering, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 10 | nos | 74000 |  |  |  |  | 740000
4 | ii | For every additional 0.1m upto 3m | 91 | nos | 1900 |  |  |  |  | 172900
4 | iii | 3m depth | 29 | nos | 96000 |  |  |  |  | 2784000
4 | iv | For every additional 0.1m upto 4m | 147 | nos | 2400 |  |  |  |  | 352800
4 | v | 4m depth | 19 | nos | 130000 |  |  |  |  | 2470000
4 | vi | For every additional 0.1m upto 5m | 54 | nos | 3100 |  |  |  |  | 167400
4 | vii | 5m depth | 1 | nos | 145000 |  |  |  |  | 145000
4 | viii | For every additional 0.1m upto 6m | 6 | nos | 3350 |  |  |  |  | 20100
3 | b | 1.8m Diameter manholes | [7 empty] | 0
4 | i | 7m depth | 1 | nos | 210000 |  |  |  |  | 210000
4 | ii | For every additional 0.1m upto 8m | 4 | nos | 3350 |  |  |  |  | 13400
2 | 19 | Providing and fixing DROP ARRANGEMENT with following dia. HDPE grade PE-100 pipes, conforming to PN 6 as per IS 14333 with latest amendments, vertical drop pipe with MS fastenings at 300 mm C/C or suitable materaial as required, with suitable expander / reducer HDPE ‘T’ joint at top with incoming sewer with one end of Tee inside the manhole closed with end cap and 45 degree bend at the bottom with HDPE specials and encasing the pipe outside the manhole with cement concrete 1:2:4 proportion, 150 / 200 mm thick alround the HDPE pipe, including vibrating, compacting, necessary centering and form work, curing, testing etc. including cost and conveyance of all materials, labour with all lead and lifts etc. complete as per specification, drawings and as directed by the Engineer in charge etc. for the followng complete with all lead and lift | [7 empty] | 0
3 | a | For 300 mm dia. incoming sewer pipe. | 25 | Rmt | 8420 |  |  |  |  | 210500
3 | b | For 350 mm to 500 mm dia. incoming sewer pipe. | 22 | Rmt | 13140 |  |  |  |  | 289080
3 | c | For 600 mm to 750 mm dia. incoming sewer pipe. | 61 | Rmt | 26325 |  |  |  |  | 1605825
2 | 20 | Dewatering the sewage or other drainage water by using minimum 5 HP pump for the diversion of storm / sewage including cost of machinery, piping upto disposal point, fuel, operator, HOM of machinery complete including diverting to the safe location as per specifications and as per the direction of the engineer with all lead and lift complete | 1152 | Hr | 185 |  |  |  |  | 213120
2 | 21 | Overpumping charges for pumping of sewage for pumping of sewage from u/s manhole to the d/s manholes or as directed including cost of machinery, piping as per site requirement, fuel, operator, HOM of machinery complete as per specifications and as per the direction of the engineer with all lead and lift | 1152 | Hr | 525 |  |  |  |  | 604800
2 | 22 | Providing sewer plugs of required sizes as per site requirement or plugging of manholes with sand / clay bags & other materials as required for the plugging/diversion of sewage from existing manholes including all required safety equipment, approvals, complete with all lead and lift and as directed | 75 | nos | 380 |  |  |  |  | 28500
2 | 23 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Dismantling Stone Masonry and Rubble stone Masonry in cement mortar as per the direction of the Engineer | 70 | Cum | 1000 |  |  |  |  | 70000
2 | 24 | Construction of dismatled size stone masonry with available stones including curing and mortar (in CM 1:6) including cost of all other required materials, required labour, machinery, curing complete with all lead and lift and as per specification and as directed | 20 | Cum | 3650 |  |  |  |  | 73000
2 | 25 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Reinforced Cement Concrete grade M20 and above as per the direction of the Engineer | 97 | Cum | 1000 |  |  |  |  | 97000
2 | 26 | KSRB 5-2.3: Providing and constructing granite/trap/basalt size stone masonry in Foundation or as required with cement mortar 1:6, stone hammered dressed in courses not less than 20cm high, bond stones at two m. apart in each course including cost of materials, labour, curing complete as per specifications. Specification No. KBS 5.1.13 complete with all lead and lift and as directed | 50 | Cum | 3650 |  |  |  |  | 182500
2 | 27 | Providing and filling in foundation/trench bottom with granite/ trap broken metal 100mm and down size with stone spalls/boulders to fill the voids, hand roller, ramming including cost of all material and labour with all lead and lifts, complete as per the specification in slushy soil for soling work complete as directed | 166 | Cum | 755 |  |  |  |  | 125330
2 | 28 | Disposing of excavated Earth of all types to a distance of upto average one side distance of 25 kilometers by vehicle including head load where ever required including loading, unloading to approved location with all lifts, labour, HOM of machinery etc. complete as per specification and as directed | 5581 | Cum | 421 |  |  |  |  | 2349601
2 | 29 (a) | Conducting the Level and Strip of Survey of alignment of Main Sewers of diameter 300mm and above, including all data required for generating GIS maps of sewer network, preparation and submission of plan & LS with ground level at 30m interval and junction points along the centre line of the alignment etc., showing the right of way, any permanent features, culverts including providing branch sewer pipeline catment survey & manhole details complete as per specifications and as directed by the Engineer in charge with all lead and lifts etc., complete for the following: for 300 mm dia | 1657 | Rmt | 18 |  |  |  |  | 29826
2 | b | Above 300 mm dia | 5460 | Rmt | 25 |  |  |  |  | 136500
2 | 30 | Providing and fixing 150mm dia Cast Iron pipe for ventilating shaft minimum 5m high with specials and cowl and with suitable grips in CC 1:2:4 pillar using 10mm to 20mm graded hard granite/trap/basalt or any other approved metal with 15cms thick cement concrete (1:2:4) around up to 1.22 mtrs above the GLR and with a foundation base of 90x90x90 cms plastered with 12 mm thick CMC 1:3 to all exposed faces and linking the shaft to the manholes by means of 15 cm dia GSW pipes and specials, jointing with tar dipped hemp 1:1½ CM caulking, curing with all lead and lifts etc., complete for all materials earth work excavation and refilling in all strata and disposal of surplus earth as directed with all lead and lifts etc., complete | 3 | nos | 21000 |  |  |  |  | 63000
2 | 31 | Providing gravel bedding for the pipe line trenches using approved granular material of size less than 25mm (murrum) including watering and consolidation by punners etc., complete with all lead and lifts, as per specification and as directed by the Engineer complete | 1418 | Cum | 480 |  |  |  |  | 680640
2 | 32 | Providing Bedding or Backfillling using approved stone dust/quarry dust of size not exceeding 5.6mm for the pipe line trenches including watering and consolidation to 95% proctor density etc., complete with all lead and lifts as per specification and as directed by the Engineer complete | 428 | Cum | 800 |  |  |  |  | 342400
2 | 33 | Provide murrum bedding for the pipeline trenches in black cotton and rock reaches or as per site requirement including watering and consolidation by punners etc. complete with all lead and lift and as directed complete | 214 | Cum | 209 |  |  |  |  | 44726
2 | 34 | KSRRB M200-14.1. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications. MORTH Specification No. 202 for Dismantling brick In cement mortar as as per the direction of the Engineer | 50 | Cum | 220 |  |  |  |  | 11000
2 | 35 | KSRB 6-2 : Providing and constructing burnt brick masonry with approved quality of non-modular bricks of standard size of class designation 5.0 Newton per sqmm (table moulded) with cement mortar 1:6 for basement and superstructure including cost of materials, labour charges, scaffolding, curing complete as per specifications. Specification No. KBS 6.2 complete with all lead and lift and as directed by the Engineer | 50 | Cum | 5820 |  |  |  |  | 291000
2 | 36 | Removing B.S. slabs of Drain and stacking with all lead and lifts as directed by the Engineer | 250 | Sqm | 55 |  |  |  |  | 13750
2 | 37 | Refixing of the available stone slabs of drains including other required materials and pointing in C.M. (1:3) with all lead and lifts complete and as directed by the Engineer complete | 250 | Sqm | 67 |  |  |  |  | 16750
2 | 38 | Providing granite slabs of 7.50 cms thick of selected quality roughly dressed and fixed in cement mortar (1:6), including pointing, curing etc complete with all lead and lifts as per specification and as directed by the Engineer . | 200 | Sqm | 548 |  |  |  |  | 109600
2 | 39 | Supplying to work spot rolling, lowering and placing in position RCC perforated rings in the already excavated pit including loading and unloading at both the destinations with all lead and lift etc., complete for soak pits including removal/dismantling of existing soak pits including disposal of unserviseble materials with all lead and lift complete | 10 | Each | 6290 |  |  |  |  | 62900
2 | 40 | Making bore in manholes without damaging the existing manholes, fixing the pipe of any diameter in line and level with CC 1:2:4, plastering the outer and inner surface in CM 1:3 including curing etc. using Sulphate Resistant Cement including disposal of debris. The cost includes the cost of materials, labour charges, lead and lifts etc. complete as per specifications and as directed by the Engineer. | 37 | nos | 180 |  |  |  |  | 6660
2 | 41 | Removing manhole cover and frame carefully and refixing the same in CC 1:2:4 band and finishing as per drawings complete with all lead and lift including disposal of the unserviceble materials complete as directed | 37 | nos | 2000 |  |  |  |  | 74000
2 | 42 | Removing of kerb stones carefully and resetting, rifixing of the kerb stones after completion of works and as directed complete with all lead and lift as per the specification | 2370 | m | 56 |  |  |  |  | 132720
2 | 43 (a) | KSRB 14.6 : Providing and laying with new heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications Specification No. KBS with all lead and lift and as directed complete | 237 | Sqm | 900 |  |  |  |  | 213300
2 | b | KSRB 14.6 : Providing and laying with available heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications. Specification No. KBS with all lead and lift and as per specification | 2133 | Sqm | 450 |  |  |  |  | 959850
2 | 44 | Cutting of trees of the following girths, including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in depression/pits etc. including labour charges, all lead and lifts etc. all as per specifications and instructions of the Engineer in charge. MOST specification 201 for the following | [7 empty] | 0
3 | a | For trees of 300 mm to 600 mm girth | 15 | nos | 76 |  |  |  |  | 1140
3 | b | For trees of 600 mm to 1200 mm girth | 15 | nos | 95 |  |  |  |  | 1425
2 | 45 | KSRB M 300-54, Construction of embankment with approved new material with all lead and lift graded and compacted to meet requirement of table 300-2 complete as per Specification which includes watering & compaction by virbratory roller/ramper/plate vibrator. MOSRTH Specification No.305 complete | 1963 | Cum | 180 |  |  |  |  | 353340
2 | 46 | Provide bedding using approved stone dust / quarry dust of size not exceeding 5.6 mm for the pipe lines trenches including watering and consolidation to 95% proctor density etc. complete with all lead and lifts as per specifications and as directed by the Engineer complete | 1963 | Cum | 805 |  |  |  |  | 1580215
2 | 47 | Construction of granular sub-base Grading-V as Sub-base and drainage layer by providing coarse graded crushed stone aggregates of granite/trap/basalt material, mixing by mix in place method by rotavator at OMC, spreading in uniform layers with motor grader on prepared surface and compacting with vibratory power roller to achieve the 98 % proctor density, complete as per specifications. Clause 401 of MORTH V Revision For Grade II Material or as required and directed complete with all lead and lift | 1963 | Cum | 1450 |  |  |  |  | 2846350
2 | 48 | KSRRB M400-14.1. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt of specific sizes to water bound macadam specifications including spreading in uniform thickness, hand packing, rolling with 3-wheeled steel/vibratory roller 8-10 tonnes in stages to proper grade and camber, applying and brooming requisite type of screening/binding materials to fill up the interstices of coarse aggregates, watering and compacting to the required density complete as per Specification. A. By manual means. MORTH Specification No. 404 Type B 11.2mm for grading III complete with all lead and lift complete as per specification and as directed | 197 | Cum | 1620 |  |  |  |  | 319140
2 | 49 | KSRRB M400-17. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt to wet mix macadam specifications including pre mixing the material with water at OMC in mechanical mix plant carriage of mixed materials by tipper to site, laying in uniform layers with paver in sub-base/base course on well prepared surface and compacting with vibratory roller to achieve the desired density complete as per specifications. MORTH Specification No. 406 with all lead and lift complete as per specification and as directed | 785 | Cum | 1700 |  |  |  |  | 1334500
2 | 50 | KSRRB M500-6. Providing and applying primer coat with S.S. bitumen emulsion on prepared surface of granular base such as WMM including cleaning of road surface and spraying primer at the rate of 0.60 kg / sqm using mechanical means complete as per specifications. Clause 502 of MORTH V revision with all lead and lift complete | 5231 | Sqm | 25 |  |  |  |  | 130775
2 | 51 | KSRRB 500-7. Providing and applying tack coat using 80/100 grade bitumen (VG10) on the prepared black topped surfaces at 2.5 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 5231 | Sqm | 10 |  |  |  |  | 52310
2 | 52 | KSRRB 500-9. Providing and applying tack coat using 80/100 grade bitumen (VG10) on granular base such as WBM surfaces hot bitumen primed at 4 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 1537 | Sqm | 15 |  |  |  |  | 23055
2 | 53 | KSRRB 500-11. Providing and laying bituminous macadam on prepared surface with crushed coarse aggregates as per design mix formula for base / binding course including loading of aggregates with F.E. loader, hot mixing of stone aggregates and bitumen in hot mix plant, transporting the mixed material in tipper to paver and laying mixed materials with paver finisher to the required level and grade, rolling by smooth wheeled, vibratory & tandem rollers to achieve the desired density, but excluding cost of primer / tack coat & including lead, lift and cost of all materials, labour, HOM complete as per specifications. Clause 504 of MORTH V revision do - using 40/60 TPH capacity H.M.P. with Mechanical paver Gr-II (50 mm to 75 mm or as directed) with 3.4% VG-30 Bitumen complete with all lead and lift and as directed | 262 | Cum | 6000 |  |  |  |  | 1572000
2 | 54 | KSRB M500-18, Providing and laying semi dense bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause no 508 complete in all respects as per specification with all lead and lift do using 40/60 TPH capacity HMP with Mechanical Paver Gr-II (25 mm to 30 mm or as directed ) with 5% VG-30 Bitumen compelte with all lead and lift and as per specifications | 132 | Cum | 7200 |  |  |  |  | 950400
2 | 55 | KSRRB M500-19. Providing and laying bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler, transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction in all respects complete as per specifications. Clause 507 of MORTH V revision do - using40/60 TPH capacity H.M.P. with Mechanical Paver Gr-II (30 mm to 40 mm or as directed) with 5.4% VG-30 Bitumen compelte with all lead and lift and as per specifications | 67 | Cum | 8000 |  |  |  |  | 536000
2 | 56 | KSRB 4-1.2 : Providing and laying in position plain cement concrete of Mix 1:3:6 with OPC @ minimum 220kgs, with 40mm and down size graded granite metal coarse aggregates @0.892cum and fine aggregates @ 0.465cum machine mixed, machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation including cost of all materials, formwork, labour, HOM curing complete as per specifications. Specification No. KBS 4.1, 4.2 compelte with all lead and lift and as per specifications For CC Road | 219 | Cum | 4700 |  |  |  |  | 1029300
2 | 57 | Constructing cement concrete for pavements using Grade concrete M30 over a prepared base, with OPC coarse aggregate at 0.69 cum, fine aggregates at 0.46 cum, Coarse and fine aggregate conforming to IS:383-2016, with Superplastizer at 3 lts conforming to IS 9103-2008. mixed in a concrete mixer of not less than 0.6 cum capacity and appropriate weigh batcher as per approved mix design, laid in approved fixed side form work (steel channel, laying and fixing of 125 micron thick polythene film, wedges, steel plates including levelling the form work as per drawing) & Spreading the concrete with shovels, rackers compacted using needle, screed and plate vibrator and finished with floaters in a continuous operation including provision of contraction, expansion, construction and longitudinal joints, including groove cutting charges, joint filler, separation membrane of impermiable plastic sheet of 125 micron, sealant primer, joint sealant, admixtures as approved, curing compound, finishing to lines and grades, textured with texturing machine and curing including cost of all materials, labour, hire charges of machineries, all lead & lift charges etc., complete as per specifications. do- with OPC at 360 kg/cum and coarse aggregate 0.69cum, fine aggregate 0.46cum. Excluding cost of steel complete as per specification and as directed | 437 | Cum | 6300 |  |  |  |  | 2753100
|  | Grand Total to be Carry forwarded to schedule No. SEWER 3 of Grand Summary for CP 25 | [7 empty] | 132308517

## Schedule 4
SEWER 4: Bill of Quantities for Sub-mains and Trunk Lines of Bilishivalli, Kylasanahalli and TS-228 Villages of Bytrayanapura Zone-4
Level | Item No. | Description | Quantity | Units | Rate (INR) | Duties | Ex.Work | Local Transport | GST | Amount (INR)
2 | 1 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN ALL KINDS OF SOIL MIXED WITH BOULDERS of 30cm size upto and exclusive of disintegrated rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following
3 | a | IN ALL KINDS OF SOIL MIXED WITH BOULDERS
4 | i | 0 to 2 Mts. Depth | 18173 | Cum | 265 |  |  |  |  | 4815845
4 | ii | 2 to 4 Mts. Depth | 14076 | Cum | 305 |  |  |  |  | 4293180
4 | iii | 4 to 6 Mts. Depth | 7374 | Cum | 340 |  |  |  |  | 2507160
4 | iv | 6 to 8 Mts. Depth | 1351 | Cum | 400 |  |  |  |  | 540400
4 | v | 8 to 10 Mts. Depth | 20 | Cum | 500 |  |  |  |  | 10000
3 | b | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN DISINTEGRATED ROCK, SOFT ROCK, SOFT SHALE AND MEDIUM HARD ROCK COMPRISING OF LIME STONE, SAND STONE, HARD SHALE, SCHIEST, FISSURED ROCK including all types of laterite without resorting to blasting or as directed including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 4544 | Cum | 345 |  |  |  |  | 1567680
4 | ii | 2 to 4 Mts. Depth | 3521 | Cum | 392 |  |  |  |  | 1380232
4 | iii | 4 to 6 Mts. Depth | 1845 | Cum | 442 |  |  |  |  | 815490
4 | iv | 6 to 8 Mts. Depth | 338 | Cum | 493 |  |  |  |  | 166634
4 | v | 8 to 10 Mts. Depth | 5 | Cum | 700 |  |  |  |  | 3500
3 | c | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. in hard rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 2500 | Cum | 1240 |  |  |  |  | 3100000
4 | ii | 2 to 4 Mts. Depth | 1937 | Cum | 1600 |  |  |  |  | 3099200
4 | iii | 4 to 6 Mts. Depth | 1016 | Cum | 2100 |  |  |  |  | 2133600
4 | iv | 6 to 8 Mts. Depth | 186 | Cum | 2400 |  |  |  |  | 446400
4 | v | 8 to 10 Mts. Depth | 5 | Cum | 3200 |  |  |  |  | 16000
3 | d | Excavation of hard rock by using Machinery like Generator, Hitachi, Breaker, Compressor, Diamond Rope with MS rods or as directed etc. with all lead and lift complete as per specifications and drawings and as directed including utility restoration, clearing and grubbing with all lead and lift as per drawings & specification and as directed | 2050 | Cum | 4400 |  |  |  |  | 9020000
2 | 2 | Providing, erecting and removing casurina pole three tier BARRICADING using poles of 7.5 to 10 cms dia or as required and minimum 1.5M height above ground fixed vertically at intervals of 2.0 to 2.5 M centre to centre or as required and horizontally at 0.5M above ground level or as required, including fixing poles in ground for a maximum depth of 0.3M and tied with coir rope firmly including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed | 9317 | Rmt | 44 |  |  |  |  | 409948
2 | 3 | Refilling of available earth around pipelines, in layers not exceeding 20 cms in depth, compacting each deposited layer by ramming after watering all lead and lift including cost of all labour including consolidation by mechanical or manual means as approved by Engineer, when earth is at suitable moisture content with desired field density upto 95% maximum dry density (modified heavy proctor test) for restoration of roads without settlement including HOM of machineries, complete. (The contractor shall take care while consolidating the earth, so that, pipes laid are not damaged due to mechanical compaction and shall restore the damaged pipes at his own cost, in case of damage) with all lead and lift and as directed complete | 45207 | Cum | 110 |  |  |  |  | 4972770
2 | 4 | Extra charges for excavation in all classifications in watery situations or foul conditions as under towards dewatering with all recuperation rates with all lead including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed until completion of the works for the following - 0 to 2 Mtr. Depth | 14369 | Cum | 52 |  |  |  |  | 747188
3 | a | 2 to 4 m depth | 6944 | Cum | 77 |  |  |  |  | 534688
3 | b | 4 to 6 m depth | 4285 | Cum | 104 |  |  |  |  | 445640
3 | c | 6 to 8 m depth | 796 | Cum | 130 |  |  |  |  | 103480
3 | d | 8 to 10 m depth | 3 | Cum | 200 |  |  |  |  | 600
2 | 5 | Cutting road surface for pipeline trenches as per specifications and as directed and including disposing off the unserviceble excavated stuff as directed including barricading, danger lighting etc, in the following classifications with all lead and lift and as directed for the following | [7 empty] | 0
3 | a | Cutting asphalt road | 1670 | Cum | 759 |  |  |  |  | 1267530
3 | b | Cutting CC Road | 419 | Cum | 1200 |  |  |  |  | 502800
2 | 6 | Providing and laying Plain Cement Concrete 1:2:4 of specified grade for foundations (screed layer) with 20 mm and down size of approved gradation hard broken granite, trap basalt or with any other approved hard aggregate including cost and conveyance of all materials, lead and lifts, plywood / steel form works, machine mixing, laying, tamping, curing etc. complete and as per specification and as directed for the following | [7 empty] | 0
3 | a | For Bedding of Sewer Pipes and other works | 219 | Cum | 4000 |  |  |  |  | 876000
2 | 7 | Providing and laying plain/reinforced cement concrete for side drains using M20 nominal mix concrete with OPC at minimum 300 kgs with 20 mm and down size granite metal coarse aggregates at 0.69 cum and fine aggregates at 0.43 cum as per desing mix, machine mixed, well compacted for walls and bottom including centering, shuttering, cost of materials, HOM of machinery, curing etc.,complete including cost of admixuture excluding cost of steel as per MORTH specification No. 1500, 1700, 2200. including cost of materials, labout, HOM complete as per specifications for raft and walls of SWD works or other works as directed | 154 | Cum | 6160 |  |  |  |  | 948640
2 | 8 | Providing and laying cement concrete 1:1.5:3 proportion for RCC works of raft, footings, encasing of pipes or other works as directed with 20 mm and down size of approved gradation hard broken granite, trap, basalt or with any other approved hard aggregate including machine mixing, cost and conveyance of all materials with all lead and lifts including plywood / steel form work, machine mixing, laying in layers of 15 cm, compacted, curing, smooth finishing etc. complete with all lead and lift and as directed (excluding the cost of reinforcement). For Encasement | 1263 | Cum | 5000 |  |  |  |  | 6315000
2 | 9 | KSRB 4-9.2: Providing TMT Fe 500 steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications with all lead and lift complete. Specification No. KBS 4.6.3 | 61925 | Kgs | 49 |  |  |  |  | 3034325
2 | 10 | KSRRB M700-4. Providing and Laying Boulder Apron in Crates of Synthetic Geogrids:- Providing, preparing and laying of geogrids crated apron of required thickness including excavation and backfilling with geogrids having characteristics as per clause 700.4.2, joining sides with connectors/ring staples or as required, top corners to be tie tensioned or as required, placing of suitable cross interval ties in layers of 300 mm or as required connecting opposite side with lateral braces and tied with polymer braids to avoid bulging, constructed as per clause 700.4.3. filled with stone as per specification for providing aroud the sewer pipe for pipe bedding/anchoring and as per specifications. For Pipe bedding in water logged area | 150 | Cum | 3650 |  |  |  |  | 547500
2 | 11 (a) | Providing Precast anti floatation blocks of RCC M20 grade concrete including casting at yard, including cost of reinforcement, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site, including providing and fixing of anchor bolts during precasting including cost of erection of anti floatation block below the sewer pipe and fixing of the steel strips as per requirement (including cost of steel strip for fixing of minimum 32mm wide and minimum 8 mm thick) including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 30 | Cum | 5550 |  |  |  |  | 166500
2 | b | Providing, driving and anchoring minimum 8 mm diameter minimum HYSD FE 500 reinforcement including cost of bending, driving, sharpening the edge for driving including cost of material, labour and other materials required as per drawings and specifications and as directed by the Engineer for holding the pipe in uplift situations complete with all lead and lift as per specification and as directed | 281 | m | 45 |  |  |  |  | 12645
2 | c | Providing Pre cast anti floatation slabs of RCC M20 grade concrete including casting at yard, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site including cost of steel strip of minimum 32mm wide and minimum 8 mm thick including providing and fixing of lifting hooks anchor bolts during precasting and nuts including cost of erection of anti floatation slabs below the sewer pipe and fixing of the steel strips as required including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 71 | Sqm | 5550 |  |  |  |  | 394050
2 | 12 | Providing and removing shoring and strutting for protecting both sides of pipe line trenches,where ever required, including the cost of all required materials and labour, safety requirements, including maintaining the shoring until completion of works complete as per specification NO.KBS 2.5/2.13 (for both sides single measument will be taken) with all lead and lift and as per the direction of the engineer complete | 17343 | Sqm | 460 |  |  |  |  | 7977780
2 | 13 | MS Sheet Piling - Providing and installing sheet piling for both sides of the trench for following depths, with Mild Steel Sheets not less than 6.5mm thick, stronger knife edge, recessed spreader sockets, 3" single or double wall shields, to be designed by the contractor to withstand all types of soils, maximum depths of as per the approved design drawing, including labour charges for installing and removing the sheet piling at various reaches of sewer line construction, including loading, unloading, transporting to the suitable location etc., complete with all lead and lifts (Measurement shall be taken for one side only even though it is provided for both sides) and maintaining the sheet piling until completion of works complete Above 3m Depth | 4337 | Sqm | 660 |  |  |  |  | 2862420
2 | 14 | Supplying DOUBLE WALL CORRUGATED (External annular corrugated & smooth internal wall) (DWC) of class SN 8, S & S piping system in accordance with IS 16098 (Part-2) and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, including rubber rings conforming to IS 5382 and cuts of pipes wherever necessary including jointing with all labour, lead & lifts, complete and giving necessary hydraulic test to the required pressure as per ISS (contractor will make his own arrangements for procuring water for testing) etc. for the following | [7 empty] | 0
3 | a | Pipes of SN 8, 300 mm dia. | 2098 | Rmt | 1750 |  |  |  |  | 3671500
3 | b | Pipes of SN 8, 400 mm dia. | 905 | Rmt | 2800 |  |  |  |  | 2534000
3 | c | Pipes of SN 8, 600 mm dia. | 85 | Rmt | 8000 |  |  |  |  | 680000
2 | 15 | Supplying of following diameters S&S RCC SPUN / VIBRATED CAST PIPES (REINFORCED) of NP-3 class conforming to IS 458:1988 with latest amendments manufactured using sulphate resistant cement and conveying to worksite, rolling and lowering into trenches, laying true to line and level including loading and unloading at both destinations and jointing of pipes & specials including cost of specials including perfect linking of joints with jack to correct position including cost of jointing materials i.e., rubber rings confirming to IS : 5382 for S&S RCC pipes with all lead and lifts as directed and giving necessary hydraulic test as per ISS and testing & commissioning etc., complete. (Contractor will make his own arrangements for procuring water for testing) including cost of all materials, labour complete as per specification and as directed for the following | [7 empty] | 0
3 | a | 300 | 900 | Rmt | 2250 |  |  |  |  | 2025000
3 | b | 350 | 516 | Rmt | 2800 |  |  |  |  | 1444800
3 | c | 400 | 388 | Rmt | 3350 |  |  |  |  | 1299800
3 | d | 600 | 763 | Rmt | 5000 |  |  |  |  | 3815000
3 | e | 700 | 1141 | Rmt | 5900 |  |  |  |  | 6731900
3 | f | 800 | 780 | Rmt | 7800 |  |  |  |  | 6084000
3 | g | 900 | 597 | Rmt | 8600 |  |  |  |  | 5134200
2 | 16 | Providing and laying testing and commissioning of Ductile iron pipes of class-K7 conforming to IS 8329:2000 with latest amendments, conveying to work site, rolling and lowering into trenches, laying true to line, level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, cutting of pipes wherever necessary, jointing with rubber gaskets, cleaning the socket and spigot end with soap solution, applying soft soap to the socket and spigot ends before insertion of rubber gaskets, jacking and fixing in perfect conditions etc. The cost to include soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS with all lead and lifts and cost of all jointing materials. (The contractor will make his own arrangements for water) the internal cement motor linning shall be with High Alumina Cement (HAC) internal cement mortal lining (CML) of DI pipes complete as per specification and as directed with all lead and lift complete for (For Major Storm Water Drain Crossing) for the following | [7 empty] | 0
3 | a | 300 mm dia | 150 | Rmt | 3200 |  |  |  |  | 480000
3 | b | 350 mm dia | 30 | Rmt | 3450 |  |  |  |  | 103500
3 | c | 400 mm dia | 60 | Rmt | 4800 |  |  |  |  | 288000
3 | d | 600 mm dia | 40 | Rmt | 8900 |  |  |  |  | 356000
3 | e | 700 mm dia | 50 | Rmt | 10900 |  |  |  |  | 545000
3 | f | 800 mm dia | 30 | Rmt | 14800 |  |  |  |  | 444000
3 | g | 900 mm dia | 30 | Rmt | 17900 |  |  |  |  | 537000
2 | 17 | Construction of RCC manhole chambers of RCC M 30 Grade approved type pre-cast RCC manhole chambers, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resitant cement, using RCC M 30 grade proportion with 20mm and downgraded jelly, well graded sand and reinforcement steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of house service connection, incoming and outgoing pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including excavation in all types of soil/rock, dewatering, refilling, sand bedding wherever required, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 7 | nos | 49000 |  |  |  |  | 343000
4 | ii | For every additional 0.1m upto 2m | 68 | nos | 1800 |  |  |  |  | 122400
4 | iii | 2mdepth | 19 | nos | 68000 |  |  |  |  | 1292000
4 | iv | For every additional 0.1m upto 3m | 36 | nos | 1900 |  |  |  |  | 68400
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 39 | nos | 74000 |  |  |  |  | 2886000
4 | ii | For every additional 0.1m upto 3m | 287 | nos | 2200 |  |  |  |  | 631400
4 | iii | 3m depth | 41 | nos | 98000 |  |  |  |  | 4018000
4 | iv | For every additional 0.1m upto 4m | 279 | nos | 2225 |  |  |  |  | 620775
4 | v | 4m depth | 17 | nos | 116000 |  |  |  |  | 1972000
4 | vi | For every additional 0.1m upto 5m | 89 | nos | 2250 |  |  |  |  | 200250
4 | vii | 5m depth | 16 | nos | 125000 |  |  |  |  | 2000000
4 | viii | For every additional 0.1m upto 6m | 87 | nos | 2250 |  |  |  |  | 195750
3 | c | 1.8m Diameter manholes | [7 empty] | 0
4 | i | 4m depth | 1 | nos | 140000 |  |  |  |  | 140000
4 | ii | For every additional 0.1m upto 5m | 8 | nos | 2700 |  |  |  |  | 21600
4 | iii | 5m depth | 5 | nos | 170000 |  |  |  |  | 850000
4 | iv | For every additional 0.1m upto 6m | 27 | nos | 3000 |  |  |  |  | 81000
4 | v | 6m depth | 12 | nos | 195000 |  |  |  |  | 2340000
4 | vi | For every additional 0.1m upto 7m | 69 | nos | 2600 |  |  |  |  | 179400
4 | vii | 7m depth | 3 | nos | 210000 |  |  |  |  | 630000
4 | viii | For every additional 0.1m upto 8m | 18 | nos | 2800 |  |  |  |  | 50400
3 | d | 2.4m Diameter manholes | [7 empty] | 0
4 | i | 6m depth | 2 | nos | 255000 |  |  |  |  | 510000
4 | ii | For every additional 0.1m upto 7m | 7 | nos | 3600 |  |  |  |  | 25200
2 | 18 | Cast in Situ Manholes in Drain/Nallah Edge/Road: Construction of RCC manhole chambers of M30 Grade proportion, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resistant cement, using M30 grade RCC with 20mm and downgraded jelly, well graded sand and steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including sand bedding wherever required, including earthwork in all types of soil/rock, dewatering, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 10 | nos | 47500 |  |  |  |  | 475000
4 | ii | For every additional 0.1m upto 2m | 89 | nos | 1800 |  |  |  |  | 160200
4 | iii | 2mdepth | 4 | nos | 68000 |  |  |  |  | 272000
4 | iv | For every additional 0.1m upto 3m | 7 | nos | 1800 |  |  |  |  | 12600
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 2 | nos | 74000 |  |  |  |  | 148000
4 | ii | For every additional 0.1m upto 3m | 14 | nos | 1900 |  |  |  |  | 26600
4 | iii | 3m depth | 12 | nos | 93000 |  |  |  |  | 1116000
4 | iv | For every additional 0.1m upto 4m | 50 | nos | 2200 |  |  |  |  | 110000
4 | v | 4m depth | 11 | nos | 130000 |  |  |  |  | 1430000
4 | vi | For every additional 0.1m upto 5m | 72 | nos | 3000 |  |  |  |  | 216000
4 | vii | 5m depth | 3 | nos | 142000 |  |  |  |  | 426000
4 | viii | For every additional 0.1m upto 6m | 14 | nos | 3200 |  |  |  |  | 44800
3 | c | 1.8m Diameter manholes | [7 empty] | 0
4 | i | 4m depth | 4 | nos | 150000 |  |  |  |  | 600000
4 | ii | For every additional 0.1m upto 5m | 37 | nos | 3000 |  |  |  |  | 111000
4 | iii | 5m depth | 2 | nos | 180000 |  |  |  |  | 360000
4 | iv | For every additional 0.1m upto 6m | 3 | nos | 3300 |  |  |  |  | 9900
4 | v | 6m depth | 3 | nos | 210000 |  |  |  |  | 630000
4 | vi | For every additional 0.1m upto 7m | 11 | nos | 3300 |  |  |  |  | 36300
4 | vii | 7m depth | 2 | nos | 212000 |  |  |  |  | 424000
4 | viii | For every additional 0.1m upto 8m | 10 | nos | 3300 |  |  |  |  | 33000
2 | 19 | Providing and fixing DROP ARRANGEMENT with following dia. HDPE grade PE-100 pipes, conforming to PN 6 as per IS 14333 with latest amendments, vertical drop pipe with MS fastenings at 300 mm C/C or suitable materaial as required, with suitable expander / reducer HDPE ‘T’ joint at top with incoming sewer with one end of Tee inside the manhole closed with end cap and 45 degree bend at the bottom with HDPE specials and encasing the pipe outside the manhole with cement concrete 1:2:4 proportion, 150 / 200 mm thick alround the HDPE pipe, including vibrating, compacting, necessary centering and form work, curing, testing etc. including cost and conveyance of all materials, labour with all lead and lifts etc. complete as per specification, drawings and as directed by the Engineer in charge etc. for the followng complete with all lead and lift | [7 empty] | 0
3 | a | For 300 mm dia. incoming sewer pipe. | 46 | Rmt | 8420 |  |  |  |  | 387320
3 | b | For 350 mm to 500 mm dia. incoming sewer pipe. | 28 | Rmt | 13140 |  |  |  |  | 367920
3 | c | For 600 mm to 750 mm dia. incoming sewer pipe. | 30 | Rmt | 26325 |  |  |  |  | 789750
3 | d | For 800 mm to 900 mm dia. incoming sewer pipe. | 21 | Rmt | 40700 |  |  |  |  | 854700
2 | 20 | Dewatering the sewage or other drainage water by using minimum 5 HP pump for the diversion of storm / sewage including cost of machinery, piping upto disposal point, fuel, operator, HOM of machinery complete including diverting to the safe location as per specifications and as per the direction of the engineer with all lead and lift complete | 1344 | Hr | 185 |  |  |  |  | 248640
2 | 21 | Overpumping charges for pumping of sewage for pumping of sewage from u/s manhole to the d/s manholes or as directed including cost of machinery, piping as per site requirement, fuel, operator, HOM of machinery complete as per specifications and as per the direction of the engineer with all lead and lift | 1344 | Hr | 525 |  |  |  |  | 705600
2 | 22 | Providing sewer plugs of required sizes as per site requirement or plugging of manholes with sand / clay bags & other materials as required for the plugging/diversion of sewage from existing manholes including all required safety equipment, approvals, complete with all lead and lift and as directed | 88 | nos | 380 |  |  |  |  | 33440
2 | 23 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Dismantling Stone Masonry and Rubble stone Masonry in cement mortar as per the direction of the Engineer | 105 | Cum | 1000 |  |  |  |  | 105000
2 | 24 | Construction of dismatled size stone masonry with available stones including curing and mortar (in CM 1:6) including cost of all other required materials, required labour, machinery, curing complete with all lead and lift and as per specification and as directed | 30 | Cum | 3650 |  |  |  |  | 109500
2 | 25 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Reinforced Cement Concrete grade M20 and above as per the direction of the Engineer | 154 | Cum | 1000 |  |  |  |  | 154000
2 | 26 | KSRB 5-2.3: Providing and constructing granite/trap/basalt size stone masonry in Foundation or as required with cement mortar 1:6, stone hammered dressed in courses not less than 20cm high, bond stones at two m. apart in each course including cost of materials, labour, curing complete as per specifications. Specification No. KBS 5.1.13 complete with all lead and lift and as directed | 75 | Cum | 3650 |  |  |  |  | 273750
2 | 27 | Providing and filling in foundation/trench bottom with granite/ trap broken metal 100mm and down size with stone spalls/boulders to fill the voids, hand roller, ramming including cost of all material and labour with all lead and lifts, complete as per the specification in slushy soil for soling work complete as directed | 252 | Cum | 785 |  |  |  |  | 197820
2 | 28 | Disposing of excavated Earth of all types to a distance of upto average one side distance of 25 kilometers by vehicle including head load where ever required including loading, unloading to approved location with all lifts, labour, HOM of machinery etc. complete as per specification and as directed | 6020 | Cum | 421 |  |  |  |  | 2534420
2 | 29 (a) | Conducting the Level and Strip of Survey of alignment of Main Sewers of diameter 300mm and above, including all data required for generating GIS maps of sewer network, preparation and submission of plan & LS with ground level at 30m interval and junction points along the centre line of the alignment etc., showing the right of way, any permanent features, culverts including providing branch sewer pipeline catment survey & manhole details complete as per specifications and as directed by the Engineer in charge with all lead and lifts etc., complete for the following: for 300 mm dia | 2998 | Rmt | 18 |  |  |  |  | 53964
2 | b | Above 300 mm dia | 5175 | Rmt | 25 |  |  |  |  | 129375
2 | 30 | Providing and fixing 150mm dia Cast Iron pipe for ventilating shaft minimum 5m high with specials and cowl and with suitable grips in CC 1:2:4 pillar using 10mm to 20mm graded hard granite/trap/basalt or any other approved metal with 15cms thick cement concrete (1:2:4) around up to 1.22 mtrs above the GLR and with a foundation base of 90x90x90 cms plastered with 12 mm thick CMC 1:3 to all exposed faces and linking the shaft to the manholes by means of 15 cm dia GSW pipes and specials, jointing with tar dipped hemp 1:1½ CM caulking, curing with all lead and lifts etc., complete for all materials earth work excavation and refilling in all strata and disposal of surplus earth as directed with all lead and lifts etc., complete | 3 | nos | 21000 |  |  |  |  | 63000
2 | 31 | Providing gravel bedding for the pipe line trenches using approved granular material of size less than 25mm (murrum) including watering and consolidation by punners etc., complete with all lead and lifts, as per specification and as directed by the Engineer complete | 2037 | Cum | 480 |  |  |  |  | 977760
2 | 32 | Providing Bedding or Backfillling using approved stone dust/quarry dust of size not exceeding 5.6mm for the pipe line trenches including watering and consolidation to 95% proctor density etc., complete with all lead and lifts as per specification and as directed by the Engineer complete | 492 | Cum | 795 |  |  |  |  | 391140
2 | 33 | Provide murrum bedding for the pipeline trenches in black cotton and rock reaches or as per site requirement including watering and consolidation by punners etc. complete with all lead and lift and as directed complete | 247 | Cum | 209 |  |  |  |  | 51623
2 | 34 | KSRRB M200-14.1. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications. MORTH Specification No. 202 for Dismantling brick In cement mortar as as per the direction of the Engineer | 75 | Cum | 220 |  |  |  |  | 16500
2 | 35 | KSRB 6-2 : Providing and constructing burnt brick masonry with approved quality of non-modular bricks of standard size of class designation 5.0 Newton per sqmm (table moulded) with cement mortar 1:6 for basement and superstructure including cost of materials, labour charges, scaffolding, curing complete as per specifications. Specification No. KBS 6.2 complete with all lead and lift and as directed by the Engineer | 75 | Cum | 5820 |  |  |  |  | 436500
2 | 36 | Removing B.S. slabs of Drain and stacking with all lead and lifts as directed by the Engineer | 375 | Sqm | 55 |  |  |  |  | 20625
2 | 37 | Refixing of the available stone slabs of drains including other required materials and pointing in C.M. (1:3) with all lead and lifts complete and as directed by the Engineer complete | 375 | Sqm | 67 |  |  |  |  | 25125
2 | 38 | Providing granite slabs of 7.50 cms thick of selected quality roughly dressed and fixed in cement mortar (1:6), including pointing, curing etc complete with all lead and lifts as per specification and as directed by the Engineer . | 300 | Sqm | 548 |  |  |  |  | 164400
2 | 39 | Supplying to work spot rolling, lowering and placing in position RCC perforated rings in the already excavated pit including loading and unloading at both the destinations with all lead and lift etc., complete for soak pits including removal/dismantling of existing soak pits including disposal of unserviseble materials with all lead and lift complete | 15 | Each | 6290 |  |  |  |  | 94350
2 | 40 | Making bore in manholes without damaging the existing manholes, fixing the pipe of any diameter in line and level with CC 1:2:4, plastering the outer and inner surface in CM 1:3 including curing etc. using Sulphate Resistant Cement including disposal of debris. The cost includes the cost of materials, labour charges, lead and lifts etc. complete as per specifications and as directed by the Engineer. | 43 | nos | 180 |  |  |  |  | 7740
2 | 41 | Removing manhole cover and frame carefully and refixing the same in CC 1:2:4 band and finishing as per drawings complete with all lead and lift including disposal of the unserviceble materials complete as directed | 43 | nos | 2000 |  |  |  |  | 86000
2 | 42 | Removing of kerb stones carefully and resetting, rifixing of the kerb stones after completion of works and as directed complete with all lead and lift as per the specification | 5960 | m | 58 |  |  |  |  | 345680
2 | 43 (a) | KSRB 14.6 : Providing and laying with new heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications Specification No. KBS with all lead and lift and as directed complete | 596 | Sqm | 900 |  |  |  |  | 536400
2 | b | KSRB 14.6 : Providing and laying with available heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications. Specification No. KBS with all lead and lift and as per specification | 5364 | Sqm | 450 |  |  |  |  | 2413800
2 | 44 | Cutting of trees of the following girths, including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in depression/pits etc. including labour charges, all lead and lifts etc. all as per specifications and instructions of the Engineer in charge. MOST specification 201 for the following | [7 empty] | 0
3 | a | For trees of 300 mm to 600 mm girth | 15 | nos | 76 |  |  |  |  | 1140
3 | b | For trees of 600 mm to 1200 mm girth | 15 | nos | 98 |  |  |  |  | 1470
2 | 45 | KSRB M 300-54, Construction of embankment with approved new material with all lead and lift graded and compacted to meet requirement of table 300-2 complete as per Specification which includes watering & compaction by virbratory roller/ramper/plate vibrator. MOSRTH Specification No.305 complete | 2034 | Cum | 185 |  |  |  |  | 376290
2 | 46 | Provide bedding using approved stone dust / quarry dust of size not exceeding 5.6 mm for the pipe lines trenches including watering and consolidation to 95% proctor density etc. complete with all lead and lifts as per specifications and as directed by the Engineer complete | 2034 | Cum | 800 |  |  |  |  | 1627200
2 | 47 | Construction of granular sub-base Grading-V as Sub-base and drainage layer by providing coarse graded crushed stone aggregates of granite/trap/basalt material, mixing by mix in place method by rotavator at OMC, spreading in uniform layers with motor grader on prepared surface and compacting with vibratory power roller to achieve the 98 % proctor density, complete as per specifications. Clause 401 of MORTH V Revision For Grade II Material or as required and directed complete with all lead and lift | 2034 | Cum | 1425 |  |  |  |  | 2898450
2 | 48 | KSRRB M400-14.1. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt of specific sizes to water bound macadam specifications including spreading in uniform thickness, hand packing, rolling with 3-wheeled steel/vibratory roller 8-10 tonnes in stages to proper grade and camber, applying and brooming requisite type of screening/binding materials to fill up the interstices of coarse aggregates, watering and compacting to the required density complete as per Specification. A. By manual means. MORTH Specification No. 404 Type B 11.2mm for grading III complete with all lead and lift complete as per specification and as directed | 204 | Cum | 1600 |  |  |  |  | 326400
2 | 49 | KSRRB M400-17. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt to wet mix macadam specifications including pre mixing the material with water at OMC in mechanical mix plant carriage of mixed materials by tipper to site, laying in uniform layers with paver in sub-base/base course on well prepared surface and compacting with vibratory roller to achieve the desired density complete as per specifications. MORTH Specification No. 406 with all lead and lift complete as per specification and as directed | 815 | Cum | 1700 |  |  |  |  | 1385500
2 | 50 | KSRRB M500-6. Providing and applying primer coat with S.S. bitumen emulsion on prepared surface of granular base such as WMM including cleaning of road surface and spraying primer at the rate of 0.60 kg / sqm using mechanical means complete as per specifications. Clause 502 of MORTH V revision with all lead and lift complete | 5422 | Sqm | 25 |  |  |  |  | 135550
2 | 51 | KSRRB 500-7. Providing and applying tack coat using 80/100 grade bitumen (VG10) on the prepared black topped surfaces at 2.5 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 5422 | Sqm | 11 |  |  |  |  | 59642
2 | 52 | KSRRB 500-9. Providing and applying tack coat using 80/100 grade bitumen (VG10) on granular base such as WBM surfaces hot bitumen primed at 4 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 1357 | Sqm | 17 |  |  |  |  | 23069
2 | 53 | KSRRB 500-11. Providing and laying bituminous macadam on prepared surface with crushed coarse aggregates as per design mix formula for base / binding course including loading of aggregates with F.E. loader, hot mixing of stone aggregates and bitumen in hot mix plant, transporting the mixed material in tipper to paver and laying mixed materials with paver finisher to the required level and grade, rolling by smooth wheeled, vibratory & tandem rollers to achieve the desired density, but excluding cost of primer / tack coat & including lead, lift and cost of all materials, labour, HOM complete as per specifications. Clause 504 of MORTH V revision do - using 40/60 TPH capacity H.M.P. with Mechanical paver Gr-II (50 mm to 75 mm or as directed) with 3.4% VG-30 Bitumen complete with all lead and lift and as directed | 273 | Cum | 6000 |  |  |  |  | 1638000
2 | 54 | KSRB M500-18, Providing and laying semi dense bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause no 508 complete in all respects as per specification with all lead and lift do using 40/60 TPH capacity HMP with Mechanical Paver Gr-II (25 mm to 30 mm or as directed ) with 5% VG-30 Bitumen compelte with all lead and lift and as per specifications | 137 | Cum | 7000 |  |  |  |  | 959000
2 | 55 | KSRRB M500-19. Providing and laying bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler, transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction in all respects complete as per specifications. Clause 507 of MORTH V revision do - using40/60 TPH capacity H.M.P. with Mechanical Paver Gr-II (30 mm to 40 mm or as directed) with 5.4% VG-30 Bitumen compelte with all lead and lift and as per specifications | 69 | Cum | 8000 |  |  |  |  | 552000
2 | 56 | KSRB 4-1.2 : Providing and laying in position plain cement concrete of Mix 1:3:6 with OPC @ minimum 220kgs, with 40mm and down size graded granite metal coarse aggregates @0.892cum and fine aggregates @ 0.465cum machine mixed, machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation including cost of all materials, formwork, labour, HOM curing complete as per specifications. Specification No. KBS 4.1, 4.2 compelte with all lead and lift and as per specifications For CC Road | 227 | Cum | 4700 |  |  |  |  | 1066900
2 | 57 | Constructing cement concrete for pavements using Grade concrete M30 over a prepared base, with OPC coarse aggregate at 0.69 cum, fine aggregates at 0.46 cum, Coarse and fine aggregate conforming to IS:383-2016, with Superplastizer at 3 lts conforming to IS 9103-2008. mixed in a concrete mixer of not less than 0.6 cum capacity and appropriate weigh batcher as per approved mix design, laid in approved fixed side form work (steel channel, laying and fixing of 125 micron thick polythene film, wedges, steel plates including levelling the form work as per drawing) & Spreading the concrete with shovels, rackers compacted using needle, screed and plate vibrator and finished with floaters in a continuous operation including provision of contraction, expansion, construction and longitudinal joints, including groove cutting charges, joint filler, separation membrane of impermiable plastic sheet of 125 micron, sealant primer, joint sealant, admixtures as approved, curing compound, finishing to lines and grades, textured with texturing machine and curing including cost of all materials, labour, hire charges of machineries, all lead & lift charges etc., complete as per specifications. do- with OPC at 360 kg/cum and coarse aggregate 0.69cum, fine aggregate 0.46cum. Excluding cost of steel complete as per specification and as directed | 453 | Cum | 6300 |  |  |  |  | 2853900
|  | Grand Total to be Carry forwarded to schedule No. SEWER 4 of Grand Summary for CP 25 | [7 empty] | 154507853

## Schedule 5
SEWER 5: Bill of Quantities for Sub-mains and Trunk Lines of Challakere, Dasarahalli, Geddalahalli, Horamavu Agara, Rachenahalli, Raja Canal and Thanisandra Villages of Bytrayanapura Zone-5
Level | Item No. | Description | Quantity | Units | Rate (INR) | Duties | Ex.Work | Local Transport | GST | Amount (INR)
2 | 1 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN ALL KINDS OF SOIL MIXED WITH BOULDERS of 30cm size upto and exclusive of disintegrated rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following
3 | a | IN ALL KINDS OF SOIL MIXED WITH BOULDERS
4 | i | 0 to 2 Mts. Depth | 52719 | Cum | 265 |  |  |  |  | 13970535
4 | ii | 2 to 4 Mts. Depth | 28756 | Cum | 305 |  |  |  |  | 8770580
4 | iii | 4 to 6 Mts. Depth | 4577 | Cum | 340 |  |  |  |  | 1556180
4 | iv | 6 to 8 Mts. Depth | 288 | Cum | 400 |  |  |  |  | 115200
3 | b | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN DISINTEGRATED ROCK, SOFT ROCK, SOFT SHALE AND MEDIUM HARD ROCK COMPRISING OF LIME STONE, SAND STONE, HARD SHALE, SCHIEST, FISSURED ROCK including all types of laterite without resorting to blasting or as directed including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 13183 | Cum | 340 |  |  |  |  | 4482220
4 | ii | 2 to 4 Mts. Depth | 7191 | Cum | 390 |  |  |  |  | 2804490
4 | iii | 4 to 6 Mts. Depth | 1145 | Cum | 440 |  |  |  |  | 503800
4 | iv | 6 to 8 Mts. Depth | 72 | Cum | 490 |  |  |  |  | 35280
3 | c | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. in hard rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
4 | i | 0 to 2 Mts. Depth | 7252 | Cum | 1240 |  |  |  |  | 8992480
4 | ii | 2 to 4 Mts. Depth | 3956 | Cum | 1700 |  |  |  |  | 6725200
4 | iii | 4 to 6 Mts. Depth | 633 | Cum | 1900 |  |  |  |  | 1202700
4 | iv | 6 to 8 Mts. Depth | 40 | Cum | 2200 |  |  |  |  | 88000
3 | d | Excavation of hard rock by using Machinery like Generator, Hitachi, Breaker, Compressor, Diamond Rope with MS rods or as directed etc. with all lead and lift complete as per specifications and drawings and as directed including utility restoration, clearing and grubbing with all lead and lift as per drawings & specification and as directed | 4321 | Cum | 4400 |  |  |  |  | 19012400
2 | 2 | Providing, erecting and removing casurina pole three tier BARRICADING using poles of 7.5 to 10 cms dia or as required and minimum 1.5M height above ground fixed vertically at intervals of 2.0 to 2.5 M centre to centre or as required and horizontally at 0.5M above ground level or as required, including fixing poles in ground for a maximum depth of 0.3M and tied with coir rope firmly including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed | 21919 | Rmt | 44 |  |  |  |  | 964436
2 | 3 | Refilling of available earth around pipelines, in layers not exceeding 20 cms in depth, compacting each deposited layer by ramming after watering all lead and lift including cost of all labour including consolidation by mechanical or manual means as approved by Engineer, when earth is at suitable moisture content with desired field density upto 95% maximum dry density (modified heavy proctor test) for restoration of roads without settlement including HOM of machineries, complete. (The contractor shall take care while consolidating the earth, so that, pipes laid are not damaged due to mechanical compaction and shall restore the damaged pipes at his own cost, in case of damage) with all lead and lift and as directed complete | 93915 | Cum | 110 |  |  |  |  | 10330650
2 | 4 | Extra charges for excavation in all classifications in watery situations or foul conditions as under towards dewatering with all recuperation rates with all lead including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed until completion of the works for the following - 0 to 2 Mtr. Depth | 35390 | Cum | 52 |  |  |  |  | 1840280
3 | a | 2 to 4 m depth | 14325 | Cum | 78 |  |  |  |  | 1117350
3 | b | 4 to 6 m depth | 3179 | Cum | 104 |  |  |  |  | 330616
3 | c | 6 to 8 m depth | 220 | Cum | 130 |  |  |  |  | 28600
2 | 5 | Cutting road surface for pipeline trenches as per specifications and as directed and including disposing off the unserviceble excavated stuff as directed including barricading, danger lighting etc, in the following classifications with all lead and lift and as directed for the following | [7 empty] | 0
3 | a | Cutting asphalt road | 4780 | Cum | 759 |  |  |  |  | 3628020
3 | b | Cutting CC Road | 1198 | Cum | 1400 |  |  |  |  | 1677200
2 | 6 | Providing and laying Plain Cement Concrete 1:2:4 of specified grade for foundations (screed layer) with 20 mm and down size of approved gradation hard broken granite, trap basalt or with any other approved hard aggregate including cost and conveyance of all materials, lead and lifts, plywood / steel form works, machine mixing, laying, tamping, curing etc. complete and as per specification and as directed for the following | [7 empty] | 0
3 | a | For Bedding of Sewer Pipes and other works | 1223 | Cum | 4000 |  |  |  |  | 4892000
2 | 7 | Providing and laying plain/reinforced cement concrete for side drains using M20 nominal mix concrete with OPC at minimum 300 kgs with 20 mm and down size granite metal coarse aggregates at 0.69 cum and fine aggregates at 0.43 cum as per desing mix, machine mixed, well compacted for walls and bottom including centering, shuttering, cost of materials, HOM of machinery, curing etc.,complete including cost of admixuture excluding cost of steel as per MORTH specification No. 1500, 1700, 2200. including cost of materials, labour, HOM complete as per specifications for raft and walls of SWD works or other works as directed | 360 | Cum | 6189 |  |  |  |  | 2228040
2 | 8 | Providing and laying cement concrete 1:1.5:3 proportion for RCC works of raft, footings, encasing of pipes or other works as directed with 20 mm and down size of approved gradation hard broken granite, trap, basalt or with any other approved hard aggregate including machine mixing, cost and conveyance of all materials with all lead and lifts including plywood / steel form work, machine mixing, laying in layers of 15 cm, compacted, curing, smooth finishing etc. complete with all lead and lift and as directed (excluding the cost of reinforcement). For Encasement | 3648 | Cum | 5050 |  |  |  |  | 18422400
2 | 9 | KSRB 4-9.2: Providing TMT Fe 500 steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications with all lead and lift complete. Specification No. KBS 4.6.3 | 175200 | Kgs | 49 |  |  |  |  | 8584800
2 | 10 | KSRRB M700-4. Providing and Laying Boulder Apron in Crates of Synthetic Geogrids:- Providing, preparing and laying of geogrids crated apron of required thickness including excavation and backfilling with geogrids having characteristics as per clause 700.4.2, joining sides with connectors/ring staples or as required, top corners to be tie tensioned or as required, placing of suitable cross interval ties in layers of 300 mm or as required connecting opposite side with lateral braces and tied with polymer braids to avoid bulging, constructed as per clause 700.4.3. filled with stone as per specification for providing aroud the sewer pipe for pipe bedding/anchoring and as per specifications. For Pipe bedding in water logged area | 350 | Cum | 3650 |  |  |  |  | 1277500
2 | 11 (a) | Providing Precast anti floatation blocks of RCC M20 grade concrete including casting at yard, including cost of reinforcement, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site, including providing and fixing of anchor bolts during precasting including cost of erection of anti floatation block below the sewer pipe and fixing of the steel strips as per requirement (including cost of steel strip for fixing of minimum 32mm wide and minimum 8 mm thick) including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 106 | Cum | 5550 |  |  |  |  | 588300
2 | b | Providing, driving and anchoring minimum 8 mm diameter minimum HYSD FE 500 reinforcement including cost of bending, driving, sharpening the edge for driving including cost of material, labour and other materials required as per drawings and specifications and as directed by the Engineer for holding the pipe in uplift situations complete with all lead and lift as per specification and as directed | 319 | m | 45 |  |  |  |  | 14355
2 | c | Providing Pre cast anti floatation slabs of RCC M20 grade concrete including casting at yard, curing, shuttering complete including cost of reinforcement, erection at site including cost of transportation from yard to site including cost of steel strip of minimum 32mm wide and minimum 8 mm thick including providing and fixing of lifting hooks anchor bolts during precasting and nuts including cost of erection of anti floatation slabs below the sewer pipe and fixing of the steel strips as required including cost of all the other required materials complete as per drawings and specifications and as directed for different diameter of pipes complete with all lead and lift | 82 | Sqm | 5550 |  |  |  |  | 455100
2 | 12 | Providing and removing shoring and strutting for protecting both sides of pipe line trenches,where ever required, including the cost of all required materials and labour, safety requirements, including maintaining the shoring until completion of works complete as per specification NO.KBS 2.5/2.13 (for both sides single measument will be taken) with all lead and lift and as per the direction of the engineer complete | 26734 | Sqm | 455 |  |  |  |  | 12163970
2 | 13 | MS Sheet Piling - Providing and installing sheet piling for both sides of the trench for following depths, with Mild Steel Sheets not less than 6.5mm thick, stronger knife edge, recessed spreader sockets, 3" single or double wall shields, to be designed by the contractor to withstand all types of soils, maximum depths of as per the approved design drawing, including labour charges for installing and removing the sheet piling at various reaches of sewer line construction, including loading, unloading, transporting to the suitable location etc., complete with all lead and lifts (Measurement shall be taken for one side only even though it is provided for both sides) and maintaining the sheet piling until completion of works complete Above 3m Depth | 6685 | Sqm | 665 |  |  |  |  | 4445525
2 | 14 | Supplying DOUBLE WALL CORRUGATED (External annular corrugated & smooth internal wall) (DWC) of class SN 8, S & S piping system in accordance with IS 16098 (Part-2) and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, including rubber rings conforming to IS 5382 and cuts of pipes wherever necessary including jointing with all labour, lead & lifts, complete and giving necessary hydraulic test to the required pressure as per ISS (contractor will make his own arrangements for procuring water for testing) etc. for the following | [7 empty] | 0
3 | a | Pipes of SN 8, 300 mm dia. | 2601 | Rmt | 1750 |  |  |  |  | 4551750
3 | b | Pipes of SN 8, 400 mm dia. | 4188 | Rmt | 2800 |  |  |  |  | 11726400
3 | c | Pipes of SN 8, 500 mm dia. | 366 | Rmt | 4800 |  |  |  |  | 1756800
3 | d | Pipes of SN 8, 600 mm dia. | 346 | Rmt | 8000 |  |  |  |  | 2768000
2 | 15 | Supplying of following diameters S&S RCC SPUN / VIBRATED CAST PIPES (REINFORCED) of NP-3 class conforming to IS 458:1988 with latest amendments manufactured using sulphate resistant cement and conveying to worksite, rolling and lowering into trenches, laying true to line and level including loading and unloading at both destinations and jointing of pipes & specials including cost of specials including perfect linking of joints with jack to correct position including cost of jointing materials i.e., rubber rings confirming to IS : 5382 for S&S RCC pipes with all lead and lifts as directed and giving necessary hydraulic test as per ISS and testing & commissioning etc., complete. (Contractor will make his own arrangements for procuring water for testing) including cost of all materials, labour complete as per specification and as directed for the following | [7 empty] | 0
3 | a | 300 | 1530 | Rmt | 2250 |  |  |  |  | 3442500
3 | b | 350 | 1670 | Rmt | 2800 |  |  |  |  | 4676000
3 | c | 400 | 2149 | Rmt | 3350 |  |  |  |  | 7199150
3 | d | 450 | 686 | Rmt | 4100 |  |  |  |  | 2812600
3 | e | 500 | 2973 | Rmt | 4400 |  |  |  |  | 13081200
3 | f | 600 | 3526 | Rmt | 5000 |  |  |  |  | 17630000
3 | g | 700 | 2026 | Rmt | 5600 |  |  |  |  | 11345600
3 | h | 800 | 670 | Rmt | 7400 |  |  |  |  | 4958000
3 | i | 900 | 1290 | Rmt | 8500 |  |  |  |  | 10965000
2 | 16 | Providing and laying testing and commissioning of Ductile iron pipes of class-K7 conforming to IS 8329:2000 with latest amendments, conveying to work site, rolling and lowering into trenches, laying true to line, level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, cutting of pipes wherever necessary, jointing with rubber gaskets, cleaning the socket and spigot end with soap solution, applying soft soap to the socket and spigot ends before insertion of rubber gaskets, jacking and fixing in perfect conditions etc. The cost to include soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS with all lead and lifts and cost of all jointing materials. (The contractor will make his own arrangements for water) the internal cement motor linning shall be with High Alumina Cement (HAC) internal cement mortal lining (CML) of DI pipes complete as per specification and as directed with all lead and lift complete for (For Major Storm Water Drain Crossing) for the following | [7 empty] | 0
3 | a | 300 mm dia | 250 | Rmt | 3200 |  |  |  |  | 800000
3 | b | 350 mm dia | 140 | Rmt | 3450 |  |  |  |  | 483000
3 | c | 400 mm dia | 200 | Rmt | 4800 |  |  |  |  | 960000
3 | d | 450 mm dia | 90 | Rmt | 5600 |  |  |  |  | 504000
3 | e | 500 mm dia | 210 | Rmt | 6600 |  |  |  |  | 1386000
3 | f | 600 mm dia | 280 | Rmt | 8900 |  |  |  |  | 2492000
3 | g | 700 mm dia | 150 | Rmt | 10900 |  |  |  |  | 1635000
3 | h | 800 mm dia | 30 | Rmt | 15500 |  |  |  |  | 465000
3 | i | 900 mm dia | 30 | Rmt | 18000 |  |  |  |  | 540000
2 | 17 | Construction of RCC manhole chambers of RCC M 30 Grade approved type pre-cast RCC manhole chambers, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resitant cement, using RCC M 30 grade proportion with 20mm and downgraded jelly, well graded sand and reinforcement steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of house service connection, incoming and outgoing pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including excavation in all types of soil/rock, dewatering, refilling, sand bedding wherever required, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 120 | nos | 49000 |  |  |  |  | 5880000
4 | ii | For every additional 0.1m upto 2m | 997 | nos | 1800 |  |  |  |  | 1794600
4 | iii | 2mdepth | 104 | nos | 68000 |  |  |  |  | 7072000
4 | iv | For every additional 0.1m upto 3m | 199 | nos | 1900 |  |  |  |  | 378100
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 224 | nos | 72000 |  |  |  |  | 16128000
4 | ii | For every additional 0.1m upto 3m | 1560 | nos | 2100 |  |  |  |  | 3276000
4 | iii | 3m depth | 130 | nos | 98000 |  |  |  |  | 12740000
4 | iv | For every additional 0.1m upto 4m | 538 | nos | 2200 |  |  |  |  | 1183600
4 | v | 4m depth | 40 | nos | 112000 |  |  |  |  | 4480000
4 | vi | For every additional 0.1m upto 5m | 167 | nos | 2250 |  |  |  |  | 375750
4 | vii | 5m depth | 5 | nos | 125000 |  |  |  |  | 625000
4 | viii | For every additional 0.1m upto 6m | 8 | nos | 2250 |  |  |  |  | 18000
3 | c | 2.4m Diameter manholes | [7 empty] | 0
4 | i | 6m depth | 2 | nos | 274000 |  |  |  |  | 548000
4 | ii | For every additional 0.1m upto 7m | 8 | nos | 3800 |  |  |  |  | 30400
2 | 18 | Cast in Situ Manholes in Drain/Nallah Edge/Road: Construction of RCC manhole chambers of M30 Grade proportion, constructed using form vibrators of standard type, with barricading, danger lighting and using of sight rails and bonding rods wherever necessary, shoring and strutting wherever required using sulphate resistant cement, using M30 grade RCC with 20mm and downgraded jelly, well graded sand and steel of approved quality, top concrete slab as per drawings and having wall thickness and raft thickness as in approved drawings with an offset in raft all-round the chamber as in approved drawings benching concrete with 1:6 slope towards the central drain finished smooth, including fixing and grouting of pipes, including conveying to work spot supply and fixing SFRC manhole cover and frame (Heavy Duty) conforming to IS 12592 with latest amendments, on a bed of CC 1:2:4 supplying and fixing of minimum 3mm thick encapsulated plastic footsteps (as per IS 10910) on 12mm dia. Grade Fe-415 steel bar (as per IS1786) staggered at 300mm apart as detailed in Technical specifications, including sand bedding wherever required, including earthwork in all types of soil/rock, dewatering, disposal of surplus earth, watering, curing, engraving manhole number with flow direction on the inner cylindrical surface etc., complete including cost of reinforcement steel shuttering and fabrication charges and also cost and conveyance of all materials, labour with all lead and lifts for various diameters and depths noted below. As per specification, drawing and as directed by the Engineer. | [7 empty] | 0
3 | a | 1.2m Diameter manholes | [7 empty] | 0
4 | i | 1m depth | 7 | nos | 47000 |  |  |  |  | 329000
4 | ii | For every additional 0.1m upto 2m | 64 | nos | 2000 |  |  |  |  | 128000
4 | iii | 2mdepth | 20 | nos | 68000 |  |  |  |  | 1360000
4 | iv | For every additional 0.1m upto 3m | 43 | nos | 2000 |  |  |  |  | 86000
3 | b | 1.5m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 67 | nos | 74000 |  |  |  |  | 4958000
4 | ii | For every additional 0.1m upto 3m | 438 | nos | 2100 |  |  |  |  | 919800
4 | iii | 3m depth | 41 | nos | 93000 |  |  |  |  | 3813000
4 | iv | For every additional 0.1m upto 4m | 214 | nos | 2100 |  |  |  |  | 449400
4 | v | 4m depth | 30 | nos | 128000 |  |  |  |  | 3840000
4 | vi | For every additional 0.1m upto 5m | 121 | nos | 2800 |  |  |  |  | 338800
4 | vii | 5m depth | 12 | nos | 142000 |  |  |  |  | 1704000
4 | viii | For every additional 0.1m upto 6m | 54 | nos | 3200 |  |  |  |  | 172800
3 | c | 1.8m Diameter manholes | [7 empty] | 0
4 | i | 2m depth | 1 | nos | 93000 |  |  |  |  | 93000
4 | ii | For every additional 0.1m upto 3m | 10 | nos | 2900 |  |  |  |  | 29000
4 | iii | 3m depth | 10 | nos | 120000 |  |  |  |  | 1200000
4 | iv | For every additional 0.1m upto 4m | 53 | nos | 3000 |  |  |  |  | 159000
4 | v | 4m depth | 15 | nos | 150000 |  |  |  |  | 2250000
4 | vi | For every additional 0.1m upto 5m | 79 | nos | 3100 |  |  |  |  | 244900
4 | vii | 5m depth | 1 | nos | 185000 |  |  |  |  | 185000
4 | viii | For every additional 0.1m upto 6m | 9 | nos | 3300 |  |  |  |  | 29700
4 | ix | 6m depth | 2 | nos | 215000 |  |  |  |  | 430000
4 | x | For every additional 0.1m upto 7m | 10 | nos | 5200 |  |  |  |  | 52000
2 | 19 | Providing and fixing DROP ARRANGEMENT with following dia. HDPE grade PE-100 pipes, conforming to PN 6 as per IS 14333 with latest amendments, vertical drop pipe with MS fastenings at 300 mm C/C or suitable materaial as required, with suitable expander / reducer HDPE ‘T’ joint at top with incoming sewer with one end of Tee inside the manhole closed with end cap and 45 degree bend at the bottom with HDPE specials and encasing the pipe outside the manhole with cement concrete 1:2:4 proportion, 150 / 200 mm thick alround the HDPE pipe, including vibrating, compacting, necessary centering and form work, curing, testing etc. including cost and conveyance of all materials, labour with all lead and lifts etc. complete as per specification, drawings and as directed by the Engineer in charge etc. for the followng complete with all lead and lift | [7 empty] | 0
3 | a | For 300 mm dia. incoming sewer pipe. | 65 | Rmt | 8420 |  |  |  |  | 547300
3 | b | For 350 mm to 500 mm dia. incoming sewer pipe. | 184 | Rmt | 13140 |  |  |  |  | 2417760
3 | c | For 600 mm to 750 mm dia. incoming sewer pipe. | 91 | Rmt | 26325 |  |  |  |  | 2395575
3 | d | For 800 mm to 900 mm dia. incoming sewer pipe. | 30 | Rmt | 40700 |  |  |  |  | 1221000
2 | 20 | Dewatering the sewage or other drainage water by using minimum 5 HP pump for the diversion of storm / sewage including cost of machinery, piping upto disposal point, fuel, operator, HOM of machinery complete including diverting to the safe location as per specifications and as per the direction of the engineer with all lead and lift complete | 3392 | Hr | 185 |  |  |  |  | 627520
2 | 21 | Overpumping charges for pumping of sewage for pumping of sewage from u/s manhole to the d/s manholes or as directed including cost of machinery, piping as per site requirement, fuel, operator, HOM of machinery complete as per specifications and as per the direction of the engineer with all lead and lift | 3392 | Hr | 525 |  |  |  |  | 1780800
2 | 22 | Providing sewer plugs of required sizes as per site requirement or plugging of manholes with sand / clay bags & other materials as required for the plugging/diversion of sewage from existing manholes including all required safety equipment, approvals, complete with all lead and lift and as directed | 236 | nos | 380 |  |  |  |  | 89680
2 | 23 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Dismantling Stone Masonry and Rubble stone Masonry in cement mortar as per the direction of the Engineer | 245 | Cum | 1000 |  |  |  |  | 245000
2 | 24 | Construction of dismatled size stone masonry with available stones including curing and mortar (in CM 1:6) including cost of all other required materials, required labour, machinery, curing complete with all lead and lift and as per specification and as directed | 70 | Cum | 3650 |  |  |  |  | 255500
2 | 25 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Reinforced Cement Concrete grade M20 and above as per the direction of the Engineer | 360 | Cum | 1000 |  |  |  |  | 360000
2 | 26 | KSRB 5-2.3: Providing and constructing granite/trap/basalt size stone masonry in Foundation or as required with cement mortar 1:6, stone hammered dressed in courses not less than 20cm high, bond stones at two m. apart in each course including cost of materials, labour, curing complete as per specifications. Specification No. KBS 5.1.13 complete with all lead and lift and as directed | 175 | Cum | 3650 |  |  |  |  | 638750
2 | 27 | Providing and filling in foundation/trench bottom with granite/ trap broken metal 100mm and down size with stone spalls/boulders to fill the voids, hand roller, ramming including cost of all material and labour with all lead and lifts, complete as per the specification in slushy soil for soling work complete as directed | 623 | Cum | 785 |  |  |  |  | 489055
2 | 28 | Disposing of excavated Earth of all types to a distance of upto average one side distance of 25 kilometers by vehicle including head load where ever required including loading, unloading to approved location with all lifts, labour, HOM of machinery etc. complete as per specification and as directed | 14016 | Cum | 440 |  |  |  |  | 6167040
2 | 29 (a) | Conducting the Level and Strip of Survey of alignment of Main Sewers of diameter 300mm and above, including all data required for generating GIS maps of sewer network, preparation and submission of plan & LS with ground level at 30m interval and junction points along the centre line of the alignment etc., showing the right of way, any permanent features, culverts including providing branch sewer pipeline catment survey & manhole details complete as per specifications and as directed by the Engineer in charge with all lead and lifts etc., complete for the following: for 300 mm dia | 4131 | Rmt | 18 |  |  |  |  | 74358
2 | b | Above 300 mm dia | 19890 | Rmt | 25 |  |  |  |  | 497250
2 | 30 | Providing and fixing 150mm dia Cast Iron pipe for ventilating shaft minimum 5m high with specials and cowl and with suitable grips in CC 1:2:4 pillar using 10mm to 20mm graded hard granite/trap/basalt or any other approved metal with 15cms thick cement concrete (1:2:4) around up to 1.22 mtrs above the GLR and with a foundation base of 90x90x90 cms plastered with 12 mm thick CMC 1:3 to all exposed faces and linking the shaft to the manholes by means of 15 cm dia GSW pipes and specials, jointing with tar dipped hemp 1:1½ CM caulking, curing with all lead and lifts etc., complete for all materials earth work excavation and refilling in all strata and disposal of surplus earth as directed with all lead and lifts etc., complete | 8 | Nos | 21000 |  |  |  |  | 168000
2 | 31 | Providing gravel bedding for the pipe line trenches using approved granular material of size less than 25mm (murrum) including watering and consolidation by punners etc., complete with all lead and lifts, as per specification and as directed by the Engineer complete | 5617 | Cum | 480 |  |  |  |  | 2696160
2 | 32 | Providing Bedding or Backfillling using approved stone dust/quarry dust of size not exceeding 5.6mm for the pipe line trenches including watering and consolidation to 95% proctor density etc., complete with all lead and lifts as per specification and as directed by the Engineer complete | 1445 | Cum | 795 |  |  |  |  | 1148775
2 | 33 | Provide murrum bedding for the pipeline trenches in black cotton and rock reaches or as per site requirement including watering and consolidation by punners etc. complete with all lead and lift and as directed complete | 725 | Cum | 209 |  |  |  |  | 151525
2 | 34 | KSRRB M200-14.1. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications. MORTH Specification No. 202 for Dismantling brick In cement mortar as as per the direction of the Engineer | 175 | Cum | 220 |  |  |  |  | 38500
2 | 35 | KSRB 6-2 : Providing and constructing burnt brick masonry with approved quality of non-modular bricks of standard size of class designation 5.0 Newton per sqmm (table moulded) with cement mortar 1:6 for basement and superstructure including cost of materials, labour charges, scaffolding, curing complete as per specifications. Specification No. KBS 6.2 complete with all lead and lift and as directed by the Engineer | 175 | Cum | 5800 |  |  |  |  | 1015000
2 | 36 | Removing B.S. slabs of Drain and stacking with all lead and lifts as directed by the Engineer | 875 | Sqm | 55 |  |  |  |  | 48125
2 | 37 | Refixing of the available stone slabs of drains including other required materials and pointing in C.M. (1:3) with all lead and lifts complete and as directed by the Engineer complete | 875 | Sqm | 67 |  |  |  |  | 58625
2 | 38 | Providing granite slabs of 7.50 cms thick of selected quality roughly dressed and fixed in cement mortar (1:6), including pointing, curing etc complete with all lead and lifts as per specification and as directed by the Engineer . | 700 | Sqm | 548 |  |  |  |  | 383600
2 | 39 | Supplying to work spot rolling, lowering and placing in position RCC perforated rings in the already excavated pit including loading and unloading at both the destinations with all lead and lift etc., complete for soak pits including removal/dismantling of existing soak pits including disposal of unserviseble materials with all lead and lift complete | 35 | Each | 6290 |  |  |  |  | 220150
2 | 40 | Making bore in manholes without damaging the existing manholes, fixing the pipe of any diameter in line and level with CC 1:2:4, plastering the outer and inner surface in CM 1:3 including curing etc. using Sulphate Resistant Cement including disposal of debris. The cost includes the cost of materials, labour charges, lead and lifts etc. complete as per specifications and as directed by the Engineer. | 125 | nos | 180 |  |  |  |  | 22500
2 | 41 | Removing manhole cover and frame carefully and refixing the same in CC 1:2:4 band and finishing as per drawings complete with all lead and lift including disposal of the unserviceble materials complete as directed | 125 | nos | 2000 |  |  |  |  | 250000
2 | 42 | Removing of kerb stones carefully and resetting, rifixing of the kerb stones after completion of works and as directed complete with all lead and lift as per the specification | 3774 | m | 56 |  |  |  |  | 211344
2 | 43 (a) | KSRB 14.6 : Providing and laying with new heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications Specification No. KBS with all lead and lift and as directed complete | 378 | Sqm | 840 |  |  |  |  | 317520
2 | b | KSRB 14.6 : Providing and laying with available heavy duty cobble stones 60 mm thick interlock pavers, using cement and course sand for manufacture of blocks of approved size, shape and colour with a minimum compressive strength of 281 kg per sqm over 50mm thick sand bed (average thickness) and compacting with plate vibrator having 3 tons compaction force thereby forcing part of sand underneath to come up in between joints, final compaction of paver surface joints into its final level, including cost of materials, labour and HOM complete as per specifications. Specification No. KBS with all lead and lift and as per specification | 3397 | Sqm | 450 |  |  |  |  | 1528650
2 | 44 | Diversion of water course by providing Coffer dams or bunds or islands as may be necessary for laying of sewer network including bailing out or pumping water during excavation and until completion of works etc., including cost of materials, labour, HOM complete as per specifications with all lead and lift complete as per specificaiton and as directed | 4816 | Cum | 290 |  |  |  |  | 1396640
2 | 45 | Cutting of trees of the following girths, including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in depression/pits etc. including labour charges, all lead and lifts etc. all as per specifications and instructions of the Engineer in charge. MOST specification 201 for the following | [7 empty] | 0
3 | a | For trees of 300 mm to 600 mm girth | 15 | nos | 76 |  |  |  |  | 1140
3 | b | For trees of 600 mm to 1200 mm girth | 15 | nos | 98 |  |  |  |  | 1470
2 | 46 | KSRB M 300-54, Construction of embankment with approved new material with all lead and lift graded and compacted to meet requirement of table 300-2 complete as per Specification which includes watering & compaction by virbratory roller/ramper/plate vibrator. MOSRTH Specification No.305 complete | 5930 | Cum | 180 |  |  |  |  | 1067400
2 | 47 | Provide bedding using approved stone dust / quarry dust of size not exceeding 5.6 mm for the pipe lines trenches including watering and consolidation to 95% proctor density etc. complete with all lead and lifts as per specifications and as directed by the Engineer complete | 5930 | Cum | 800 |  |  |  |  | 4744000
2 | 48 | Construction of granular sub-base Grading-V as Sub-base and drainage layer by providing coarse graded crushed stone aggregates of granite/trap/basalt material, mixing by mix in place method by rotavator at OMC, spreading in uniform layers with motor grader on prepared surface and compacting with vibratory power roller to achieve the 98 % proctor density, complete as per specifications. Clause 401 of MORTH V Revision For Grade II Material or as required and directed complete with all lead and lift | 5930 | Cum | 1400 |  |  |  |  | 8302000
2 | 49 | KSRRB M400-14.1. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt of specific sizes to water bound macadam specifications including spreading in uniform thickness, hand packing, rolling with 3-wheeled steel/vibratory roller 8-10 tonnes in stages to proper grade and camber, applying and brooming requisite type of screening/binding materials to fill up the interstices of coarse aggregates, watering and compacting to the required density complete as per Specification. A. By manual means. MORTH Specification No. 404 Type B 11.2mm for grading III complete with all lead and lift complete as per specification and as directed | 595 | Cum | 1620 |  |  |  |  | 963900
2 | 50 | KSRRB M400-17. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt to wet mix macadam specifications including pre mixing the material with water at OMC in mechanical mix plant carriage of mixed materials by tipper to site, laying in uniform layers with paver in sub-base/base course on well prepared surface and compacting with vibratory roller to achieve the desired density complete as per specifications. MORTH Specification No. 406 with all lead and lift complete as per specification and as directed | 2374 | Cum | 1650 |  |  |  |  | 3917100
2 | 51 | KSRRB M500-6. Providing and applying primer coat with S.S. bitumen emulsion on prepared surface of granular base such as WMM including cleaning of road surface and spraying primer at the rate of 0.60 kg / sqm using mechanical means complete as per specifications. Clause 502 of MORTH V revision with all lead and lift complete | 15809 | Sqm | 25 |  |  |  |  | 395225
2 | 52 | KSRRB 500-7. Providing and applying tack coat using 80/100 grade bitumen (VG10) on the prepared black topped surfaces at 2.5 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 15809 | Sqm | 11 |  |  |  |  | 173899
2 | 53 | KSRRB 500-9. Providing and applying tack coat using 80/100 grade bitumen (VG10) on granular base such as WBM surfaces hot bitumen primed at 4 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 3955 | Sqm | 17 |  |  |  |  | 67235
2 | 54 | KSRRB 500-11. Providing and laying bituminous macadam on prepared surface with crushed coarse aggregates as per design mix formula for base / binding course including loading of aggregates with F.E. loader, hot mixing of stone aggregates and bitumen in hot mix plant, transporting the mixed material in tipper to paver and laying mixed materials with paver finisher to the required level and grade, rolling by smooth wheeled, vibratory & tandem rollers to achieve the desired density, but excluding cost of primer / tack coat & including lead, lift and cost of all materials, labour, HOM complete as per specifications. Clause 504 of MORTH V revision do - using 40/60 TPH capacity H.M.P. with Mechanical paver Gr-II (50 mm to 75 mm or as directed) with 3.4% VG-30 Bitumen complete with all lead and lift and as directed | 793 | Cum | 5800 |  |  |  |  | 4599400
2 | 55 | KSRB M500-18, Providing and laying semi dense bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause no 508 complete in all respects as per specification with all lead and lift do using 40/60 TPH capacity HMP with Mechanical Paver Gr-II (25 mm to 30 mm or as directed ) with 5% VG-30 Bitumen compelte with all lead and lift and as per specifications | 398 | Cum | 7000 |  |  |  |  | 2786000
2 | 56 | KSRRB M500-19. Providing and laying bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler, transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction in all respects complete as per specifications. Clause 507 of MORTH V revision do - using40/60 TPH capacity H.M.P. with Mechanical Paver Gr-II (30 mm to 40 mm or as directed) with 5.4% VG-30 Bitumen compelte with all lead and lift and as per specifications | 201 | Cum | 7800 |  |  |  |  | 1567800
2 | 57 | KSRB 4-1.2 : Providing and laying in position plain cement concrete of Mix 1:3:6 with OPC @ minimum 220kgs, with 40mm and down size graded granite metal coarse aggregates @0.892cum and fine aggregates @ 0.465cum machine mixed, machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation including cost of all materials, formwork, labour, HOM curing complete as per specifications. Specification No. KBS 4.1, 4.2 compelte with all lead and lift and as per specifications For CC Road | 661 | Cum | 4600 |  |  |  |  | 3040600
2 | 58 | Constructing cement concrete for pavements using Grade concrete M30 over a prepared base, with OPC coarse aggregate at 0.69 cum, fine aggregates at 0.46 cum, Coarse and fine aggregate conforming to IS:383-2016, with Superplastizer at 3 lts conforming to IS 9103-2008. mixed in a concrete mixer of not less than 0.6 cum capacity and appropriate weigh batcher as per approved mix design, laid in approved fixed side form work (steel channel, laying and fixing of 125 micron thick polythene film, wedges, steel plates including levelling the form work as per drawing) & Spreading the concrete with shovels, rackers compacted using needle, screed and plate vibrator and finished with floaters in a continuous operation including provision of contraction, expansion, construction and longitudinal joints, including groove cutting charges, joint filler, separation membrane of impermiable plastic sheet of 125 micron, sealant primer, joint sealant, admixtures as approved, curing compound, finishing to lines and grades, textured with texturing machine and curing including cost of all materials, labour, hire charges of machineries, all lead & lift charges etc., complete as per specifications. do- with OPC at 360 kg/cum and coarse aggregate 0.69cum, fine aggregate 0.46cum. Excluding cost of steel complete as per specification and as directed | 1320 | Cum | 6000 |  |  |  |  | 7920000
2 | 59 | Conducting ground penetrating RADAR SURVEY in a corridor of 4-6 meter width to detect burred utilities like pipes, cables etc. in such corridor. Marking of the detected utilities on the map of corridor with information of locations and depth to the top of various utilities detected. Work to be conducted using 500 Mhz and 300 Mhz antenna or laterst equipment for the best possible resolution and penetration etc. complete with all lead and lift and as per the direction of the Engineer for the following | [7 empty] | 0
3 | a | Along the road crossings with dividers and upto 50 M width. | 1 | nos | 100000 |  |  |  |  | 100000
3 | b | Along the road crossings with dividers and upto 60 M width. | 2 | nos | 150000 |  |  |  |  | 300000
3 | c | Along the road crossings above 60M width for every 1 M and part thereof. | 60 | nos | 3000 |  |  |  |  | 180000
2 | 60 | Conducting Seismic Refraction survey to determine stratigraphy along proposed route i.e, soil, seathered rock, rock interfaces. Detection of faults, fractures, shear zones etc. in the investigated area. Geophone spacing 5M or as requried, test to be conducted using 24 channel signal enhancement type seismograph or as required, 5M Geophone Spacing or as required with all lead and lift and as directed | 230 | m | 600 |  |  |  |  | 138000
2 | 61 | Installation of product pipe by Auger Boring method including making entry and exit pits, all related civil works like excavation, shoring, strutting, dewatering etc, shielded excavation through auger boring process, lowering of pipe segments in the jacking pit, laying and jointing of product pipeline through jacking process from jacking pit including the cost of RCC NP3 S&S or as required pipes including dewatering and other works required for commissioning of the works in all types of soil including rock complete with all lead and lift as per specifications and as directed complete for the following | [7 empty] | 0
3 | a | 700 mm dia | 90 | Rmt | 58000 |  |  |  |  | 5220000
2 | 62 | Installation of product pipe by Micro Tunneling method including concrete structural shaft of sheet piles/RCC retaining walls/well sinking/secant piling as per respective site requirements all inclusive as per IndSTT: 102-2018: Code of Practice for Micro Tunneling & Pipe Jacking Suiting Indian Conditions including cost of RCC NP4 pipe complete including dewatering and other works required for commissioning of the works with all lead and lift as per specifications and as directed complete for the following For 1200 mm Dia | [7 empty] | 0
3 | a | All type of soil (Except mixed strata & rocks) | 20 | Rmt | 102000 |  |  |  |  | 2040000
3 | b | Mixed Strata | 20 | Rmt | 135000 |  |  |  |  | 2700000
3 | c | Rocks | 10 | Rmt | 180000 |  |  |  |  | 1800000
2 | 63 | Installation of product pipe by manual jacking method including Manufacturing, providing, transporting, rolling, lowering, laying & jointing, testing, commissioning of ERW (Electric Resistance Welded), SAW (Submerged Arc Welded) MS pipe (Fe-410 grade) conforming to IS 3589-2001 with latest amendments including perfect linking welding of joints to correct position including cost and conveyance of pipes and materials with all lead, lift, cost of labour, loading and unloading of pipes for the following diameters with specified thickness of plate as noted below including bailing out of water wherever necessary for laying of MS carrier pipe of suitable dia including inside and outside of casing pipe painted with two coats of Anti corrossive tankmastic paint. Installation of steel pipe by Ramming / Jacking method to cross Railway track/ NH/ BDA/ BBMP/ Other roads/ Existing utilities/ NALA crossings, filling the gap between casing pipe and carrier pipe with quarry grit using compressor with all necessary equipments, plants etc, complete. Suitable spacers of HDP/MS or other similar material should be provided in between carrier & casing pipe to prevent carrier pipe forming metallic contact with casing pipe. The rates are inclusive of all taxes and duties. Note: The cost of jacking is inclusive of cost of M.S. casing pipe of specified thickness. The cost of Jacking includes all leads lifts, cost of consumables, fuel charges, labour and taxes and duties excluding cost of jacking and receiving pits including cost of casing and carrier pipes complete with all lead and lift and as per detailed specification and as directed by the Engineer for the following | [7 empty] | 0
3 | a | Jacking of 900 mm dia & 16 mm thick M.S. Casing Pipe. With 600 mm DWC Pipe | 90 | Rmt | 62000 |  |  |  |  | 5580000
2 | 64 | Excavation for ramming / jacking pits and receiving pit. The work includes cutting of asphalted/ concrete surface, excavation in all types of soil including rock and strata, dewatering, disposal of debris, refiling the trenches with consolidation, including shoring & strutting, restoration of road surface to normal surface by concreting/asphalting etc., complete (cost for both inlet and exit pits) as per specification and as directed complete for the following | [7 empty] | 0
3 | a | Size up to 5 mts X 3 mts - depth up to 6 mts | 1 | nos | 190000 |  |  |  |  | 190000
|  | Grand Total to be Carry forwarded to schedule No. SEWER 5 of Grand Summary for CP 25 | [7 empty] | 409983928

## Pumping
Pumping Main: Bill of Quantities for Pumping Main for Bytrayanapura Zone
Level | Item No. | Description | Quantity | Units | Rate (INR) | Duties | Ex.Work | Local Transport | GST | Amount (INR)
2 | 1 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN ALL KINDS OF SOIL MIXED WITH BOULDERS of 30cm size upto and exclusive of disintegrated rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following
3 | a | 0 to 2 Mts. Depth | 1709 | Cum | 265 |  |  |  |  | 452885
3 | b | 2 to 4 Mts. Depth | 107 | Cum | 305 |  |  |  |  | 32635
2 | 2 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. IN DISINTEGRATED ROCK, SOFT ROCK, SOFT SHALE AND MEDIUM HARD ROCK COMPRISING OF LIME STONE, SAND STONE, HARD SHALE, SCHIEST, FISSURED ROCK including all types of laterite without resorting to blasting or as directed including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
3 | a | 0 to 2 Mts. Depth | 428 | Cum | 340 |  |  |  |  | 145520
3 | b | 2 to 4 Mts. Depth | 10.7 | Cum | 400 |  |  |  |  | 4280
2 | 3 | EXCAVATING FOR PIPE LINE TRENCHES OF REQUIRED WIDTH by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading, danger lighting, shoring, strutting, dewatering, etc. in hard rock including utility restoration, clearing and grubbing with all lead as per drawings & specification and as directed for the following | [7 empty] | 0
3 | a | 0 to 2 Mts. Depth | 107 | Cum | 1270 |  |  |  |  | 135890
3 | b | 2 to 4 Mts. Depth | 10.7 | Cum | 1900 |  |  |  |  | 20330
2 | 4 | Excavation of hard rock by using Machinery like Generator, Hitachi, Breaker, Compressor, Diamond Rope with MS rods or as directed etc. with all lead and lift complete as per specifications and drawings and as directed including utility restoration, clearing and grubbing with all lead and lift as per drawings & specification and as directed | 65 | Cum | 4400 |  |  |  |  | 286000
2 | 5 | Providing, erecting and removing casurina pole three tier BARRICADING using poles of 7.5 to 10 cms dia or as required and minimum 1.5M height above ground fixed vertically at intervals of 2.0 to 2.5 M centre to centre or as required and horizontally at 0.5M above ground level or as required, including fixing poles in ground for a maximum depth of 0.3M and tied with coir rope firmly including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed | 854 | Rmt | 50 |  |  |  |  | 42700
2 | 6 | Refilling of available earth around pipelines, in layers not exceeding 20 cms in depth, compacting each deposited layer by ramming after watering all lead and lift including cost of all labour including consolidation by mechanical or manual means as approved by Engineer, when earth is at suitable moisture content with desired field density upto 95% maximum dry density (modified heavy proctor test) for restoration of roads without settlement including HOM of machineries, complete. (The contractor shall take care while consolidating the earth, so that, pipes laid are not damaged due to mechanical compaction and shall restore the damaged pipes at his own cost, in case of damage) with all lead and lift and as directed complete | 2045.5562 | Cum | 110 |  |  |  |  | 225011.1853
2 | 7 (a) | Extra charges for excavation in all classifications in watery situations or foul conditions as under towards dewatering with all recuperation rates with all lead including cost and conveyances of all materials, labour, with all lead and lifts charges etc. complete as per specifcations and as directed until completion of the works for the following - 0 to 2 Mtr. Depth | 428 | Cum | 52 |  |  |  |  | 22256
2 | b | 2 to 4 m depth | 22 | Cum | 78 |  |  |  |  | 1716
2 | 8 | Cutting road surface for pipeline trenches as per specifications and as directed and including disposing off the unserviceble excavated stuff as directed including barricading, danger lighting etc, in the following classifications with all lead and lift and as directed for the following Cutting asphalt road Cutting asphalt road | 444 | Cum | 750 |  |  |  |  | 333000
2 | 9 | KSRB M 300-54, Construction of embankment with approved new material with all lead and lift graded and compacted to meet requirement of table 300-2 complete as per Specification which includes watering & compaction by virbratory roller/ramper/plate vibrator. MOSRTH Specification No.305 complete | 467 | Cum | 185 |  |  |  |  | 86395
2 | 10 | Provide bedding using approved stone dust / quarry dust of size not exceeding 5.6 mm for the pipe lines trenches including watering and consolidation to 95% proctor density etc. complete with all lead and lifts as per specifications and as directed by the Engineer complete | 467 | Cum | 820 |  |  |  |  | 382940
2 | 11 | Construction of granular sub-base Grading-V as Sub-base and drainage layer by providing coarse graded crushed stone aggregates of granite/trap/basalt material, mixing by mix in place method by rotavator at OMC, spreading in uniform layers with motor grader on prepared surface and compacting with vibratory power roller to achieve the 98 % proctor density, complete as per specifications. Clause 401 of MORTH V Revision For Grade II Material or as required and directed complete with all lead and lift | 311 | Cum | 1475 |  |  |  |  | 458725
2 | 12 | KSRRB M400-14.1. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt of specific sizes to water bound macadam specifications including spreading in uniform thickness, hand packing, rolling with 3-wheeled steel/vibratory roller 8-10 tonnes or as required in stages to proper grade and camber, applying and brooming requisite type of screening/binding materials to fill up the interstices of coarse aggregates, watering and compacting to the required density complete as per Specification. A. By manual means. MORTH Specification No. 404 Type B 11.2mm for grading III complete with all lead and lift complete as per specification and as directed | 47 | Cum | 1625 |  |  |  |  | 76375
2 | 13 | KSRRB M400-17. Providing, laying, spreading and compacting cushed stone aggregates of granite / trap / basalt to wet mix macadam specifications including pre mixing the material with water at OMC in mechanical mix plant carriage of mixed materials by tipper to site, laying in uniform layers with paver in sub-base/base course on well prepared surface and compacting with vibratory roller to achieve the desired density complete as per specifications. MORTH Specification No. 406 with all lead and lift complete as per specification and as directed | 187 | Cum | 1750 |  |  |  |  | 327250
2 | 14 | KSRRB M500-6. Providing and applying primer coat with S.S. bitumen emulsion on prepared surface of granular base such as WMM including cleaning of road surface and spraying primer at the rate of 0.60 kg / sqm using mechanical means complete as per specifications. Clause 502 of MORTH V revision with all lead and lift complete | 1554 | Sqm | 30 |  |  |  |  | 46620
2 | 15 | KSRRB 500-7. Providing and applying tack coat using 80/100 grade bitumen (VG10) on the prepared black topped surfaces at 2.5 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 1554 | Sqm | 13 |  |  |  |  | 20202
2 | 16 | KSRRB 500-9. Providing and applying tack coat using 80/100 grade bitumen (VG10) on granular base such as WBM surfaces hot bitumen primed at 4 kg per 10 sqm, heating bitumen in boiler fitted with spray set (excluding cleaning of road surface) including cost of all materials, labour, HOM complete as per specifications. Clause 503 of MORTH V revision compelte with all lead and lift and as per specifications | 1554 | Sqm | 20 |  |  |  |  | 31080
2 | 17 | KSRRB 500-11. Providing and laying bituminous macadam on prepared surface with crushed coarse aggregates as per design mix formula for base / binding course including loading of aggregates with F.E. loader, hot mixing of stone aggregates and bitumen in hot mix plant, transporting the mixed material in tipper to paver and laying mixed materials with paver finisher to the required level and grade, rolling by smooth wheeled, vibratory & tandem rollers to achieve the desired density, but excluding cost of primer / tack coat & including lead, lift and cost of all materials, labour, HOM complete as per specifications. Clause 504 of MORTH V revision do - using 40/60 TPH capacity H.M.P. with Mechanical paver Gr-II (50 mm to 75 mm or as directed) with 3.4% VG-30 Bitumen complete with all lead and lift and as directed | 78 | Cum | 6000 |  |  |  |  | 468000
2 | 18 | KSRB M500-18, Providing and laying semi dense bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause no 508 complete in all respects as per specification with all lead and lift do using 40/60 TPH capacity HMP with Mechanical Paver Gr-II (25 mm to 30 mm or as directed ) with 5% VG-30 Bitumen compelte with all lead and lift and as per specifications | 39 | Cum | 7200 |  |  |  |  | 280800
2 | 19 | KSRRB M500-19. Providing and laying bituminous concrete using crushed aggregates of specified grading, premixed with bituminous binder and filler, transporting the hot mix to work site, laying with a paver finisher to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction in all respects complete as per specifications. Clause 507 of MORTH V revision do - using40/60 TPH capacity H.M.P. with Mechanical Paver Gr-II (30 mm to 40 mm or as directed) with 5.4% VG-30 Bitumen compelte with all lead and lift and as per specifications | 23 | Cum | 8000 |  |  |  |  | 184000
2 | 20 | KSRRB M700-4. Providing and Laying Boulder Apron in Crates of Synthetic Geogrids:- Providing, preparing and laying of geogrids crated apron of required thickness including excavation and backfilling with geogrids having characteristics as per clause 700.4.2, joining sides with connectors/ring staples or as required, top corners to be tie tensioned or as required, placing of suitable cross interval ties in layers of 300 mm or as required connecting opposite side with lateral braces and tied with polymer braids to avoid bulging, constructed as per clause 700.4.3. filled with stone as per specification for providing aroud the sewer pipe for pipe bedding/anchoring and as per specifications. For Pipe bedding in water logged area | 200 | Cum | 3650 |  |  |  |  | 730000
2 | 21 | Providing and laying Plain Cement Concrete 1:3:6 of specified grade for foundations (screed layer) with 20 mm and down size of approved gradation hard broken granite, trap basalt or with any other approved hard aggregate including cost and conveyance of all materials, lead and lifts, plywood / steel form works, machine mixing, laying, tamping curing etc. complete: | 5 | Cum | 5100 |  |  |  |  | 25500
2 | 22 | Providing and laying Plain Cement Concrete 1:2:4 of specified grade for foundations (screed layer) with 20 mm and down size of approved gradation hard broken granite, trap basalt or with any other approved hard aggregate including cost and conveyance of all materials, lead and lifts, plywood / steel form works, machine mixing, laying, tamping curing etc. complete: For Anchor, thrust blocks and Pipe Bedding | 128.331 | Cum | 6000 |  |  |  |  | 769986
2 | 23 | Providing and laying cement concrete 1:1.5:3 proportion for RCC works of raft, footings etc. for ground level reservoir with 20 mm and down size of approved gradation hard broken granite, trap, basalt or with any other approved hard aggregate including machine mixing, cost and conveyance of all materials with all lead and lifts including plywood / steel form work, machine mixing, laying in layers of 15 cm., compacted, curing, smooth finishing etc. complete (excluding the cost of reinforcement). for encasement of pumping main/ sewers and other works | 49.4838 | Cum | 5900 |  |  |  |  | 291954.3979
2 | 24 | KSRB 4-9.2: Providing TMT Fe 500 steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications with all lead and lift complete. Specification No. KBS 4.6.3 For Storm Water Drain - Restoration, Achor, thrust blocks & Encasing | 11658.5637 | Kgs | 65 |  |  |  |  | 757806.6405
2 | 25 | Providing and laying Ductile iron pipes of class-K9 conforming to IS 8329:2000 with latest amendments, conveying to work site, rolling and lowering into trenches, laying true to line, level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations, cutting of pipes wherever necessary, jointing with DI specials (including cost of specials) and rubber gaskets, cleaning the socket and spigot end with soap solution, applying soft soap to the socket and spigot ends before insertion of rubber gaskets, jacking and fixing in perfect conditions etc. The cost to include soap solution, soft soap, waste etc. and giving necessary hydraulic test to the required pressure as per ISS with all lead and lifts and cost of all jointing materials. (The contractor will make his own arrangements for water for testing. Earth work excavation in trenches and jointing of pipes to be measured and paid for separately) for internal cement mortal lining (CML) of DI pipes, High Alumina Cement (HAC) shall be provided for the following | [7 empty] | 0
3 | a | Ductile Iron Pipe Class K-9 250 mm dia. | 1575 | Rmt | 5000 |  |  |  |  | 7875000
3 | b | Ductile Iron Pipe Class K-9 350 mm dia. | 132 | Rmt | 6600 |  |  |  |  | 871200
2 | 26 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Dismantling Stone Masonry and Rubble stone Masonry in cement mortar as per the direction of the Engineer | 20 | Cum | 900 |  |  |  |  | 18000
2 | 27 | Construction of dismatled size stone masonry with available stones including curing and mortar (in CM 1:6) including cost of all other required materials, required labour, machinery, curing complete with all lead and lift and as per specification and as directed | 10 | Cum | 3650 |  |  |  |  | 36500
2 | 28 | KSRRB M200-15.2. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement conrete, wood work, steel work, including T&P and scaffolding wherever necessary. Sorting the dismantled material. Disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications for Reinforced Cement Concrete grade M20 and above as per the direction of the Engineer | 20 | Cum | 1000 |  |  |  |  | 20000
2 | 29 | KSRRB M200-14.1. Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonry, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary, sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications. MORTH Specification No. 202 for Dismantling brick In cement mortar as as per the direction of the Engineer | 10 | Cum | 225 |  |  |  |  | 2250
2 | 30 | KSRB 6-2 : Providing and constructing burnt brick masonry with approved quality of non-modular bricks of standard size of class designation 5.0 Newton per sqmm (table moulded) with cement mortar 1:6 for basement and superstructure including cost of materials, labour charges, scaffolding, curing complete as per specifications. Specification No. KBS 6.2 complete with all lead and lift and as directed by the Engineer | 10 | Cum | 5800 |  |  |  |  | 58000
2 | 31 | KSRB 5-2.3: Providing and constructing granite/trap/basalt size stone masonry in Foundation or as required with cement mortar 1:6, stone hammered dressed in courses not less than 20cm high, bond stones at two m. apart in each course including cost of materials, labour, curing complete as per specifications. Specification No. KBS 5.1.13 complete with all lead and lift and as directed | 10 | Cum | 3650 |  |  |  |  | 36500
2 | 32 | Providing and filling in foundation/trench bottom with granite/ trap broken metal 100mm and down size with stone spalls/boulders to fill the voids, hand roller, ramming including cost of all material and labour with all lead and lifts, complete as per the specification in slushy soil for soling work complete as directed | 129 | Cum | 800 |  |  |  |  | 103200
2 | 33 | Disposing of excavated Earth of all types to a distance of upto average one side distance of 25 kilometers (minimum) by vehicle including head load where ever required including loading, unloading to approved location with all lifts, labour, HOM of machinery etc. complete as per specification and as directed | 391.8438 | Cum | 415 |  |  |  |  | 162615.1644
2 | 34 (a) | Conducting the Level and Strip of Survey of alignment of Main Sewers of diameter 300mm and above, including all data required for generating GIS maps of sewer network, preparation and submission of plan & LS with ground level at 30m interval and junction points along the centre line of the alignment etc., showing the right of way, any permanent features, culverts including providing branch sewer pipeline catment survey & manhole details complete as per specifications and as directed by the Engineer in charge with all lead and lifts etc., complete for the following: for 300 mm dia | 1575 | Rmt | 17 |  |  |  |  | 26775
2 | b | Above 300 mm dia | 132 | Rmt | 24 |  |  |  |  | 3168
2 | 35 | Providing gravel bedding for the pipe line trenches using approved granular material of size less than 25mm (murrum) including watering and consolidation by punners etc., complete with all lead and lifts, as per specification and as directed by the Engineer complete | 69 | Cum | 500 |  |  |  |  | 34500
2 | 36 | Providing Bedding or Backfillling using approved stone dust/quarry dust of size not exceeding 5.6mm for the pipe line trenches including watering and consolidation to 95% proctor density etc., complete with all lead and lifts as per specification and as directed by the Engineer complete | 69 | Cum | 800 |  |  |  |  | 55200
2 | 37 | Provide murrum bedding for the pipeline trenches in black cotton and rock reaches or as per site requirement including watering and consolidation by punners etc. complete with all lead and lift and as directed complete | 35 | Cum | 200 |  |  |  |  | 7000
2 | 38 | Removing B.S. slabs of Drain and stacking with all lead and lifts as directed by the Engineer | 100 | Sqm | 53 |  |  |  |  | 5300
2 | 39 | Refixing of the available stone slabs of drains including other required materials and pointing in C.M. (1:3) with all lead and lifts complete and as directed by the Engineer complete | 100 | Sqm | 70 |  |  |  |  | 7000
2 | 40 | Providing granite slabs of 7.50 cms thick of selected quality roughly dressed and fixed in cement mortar (1:6), including pointing, curing etc complete with all lead and lifts as per specification and as directed by the Engineer . | 100 | Sqm | 574.22 |  |  |  |  | 57422
2 | 41 | Supply, fixing, testing, commissioning and delivery of Resilient seated soft sealing SLUICE VALVE/SCOUR VALVE of PN 10 of various dia with specials, with body, bonnet of ductile iron (DI) of grade GGG50, wedge fully rubber lined with EPDM and seals of NBR and the valves should be vacuum tight and 100% lead proof with face dimensions as per BS 5163-89 / IS 14846-2000 / DIN 3202 F4/F5 including scour pipe if required. The stem sealing should be with Toroidal sealing rings (minimum 2 “O” rings). All the valves should be with electrostatic powder coating both inside and outside with pocket less body passage including cost of DI specials and other required materials complete with all lead and lift and as per drawings, specifications and as directed . The valves shall be supplied with suitable size galvanized bolts and nuts of required numbers as per relevant IS. for the following For 250 mm dia | 2 | Each | 100000 |  |  |  |  | 200000
2 | 42 | Supply, fixing, testing and commissioning of single chamber triple function tamper proof (Both the orifices to be housed in the single chamber) AIR VALVES of PN 10 with isolation valve & specials with Body and cover in Ductile cast iron of grade GGG-50 including isolation valve complete. All internal parts such as float, shell etc., all cover bolts of austenitic alloy / SS 304 steel, DN 50 float of HOSTAFLON / SSRAL5005. The valves should be designed for all the three functions i.e., 1. Large orifice for venting of large air volumes on start up. 2. Large orifice for intake of large air volumes. 3. Small orifice for discharge of pressurized air during operation including cost of all DI specials and other materials required complete with all lead and lift and as directed complete for the following For 80 mm dia | 2 | Each | 44000 |  |  |  |  | 88000
2 | 43 | Construction of Valve Chambers RCC valve chamber including excavation in all types of soil including rock, refilling, dewatering, including laying of PCC below raft slab of minimum 10 cm thick, incluidng constrution of RCC works in minimum M 25 grade concrete, raft minimum 200 mm thick, side walls with minimum 150 mm thick and cover slab minimum 200 mm thick including cost of concrete and reinforcement, including dispoal of surplus earth, the cover slab shall be cast in situ or pracast concrete slabs including all lead and lift complete of minimum 1. 5 m x 1. 5 m (inside dimensions) and depth as per site requirement as per the direction of the engineer and as directed | 4 | Each | 72000 |  |  |  |  | 288000
2 | 44 | Supplying to work spot rolling, lowering and placing in position RCC perforated rings in the already excavated pit including loading and unloading at both the destinations with all lead and lift etc., complete for soak pits including removal/dismantling of soak pits including disposal of unserviseble materials with all lead and lift complete | 5 | Each | 6300 |  |  |  |  | 31500
2 | 45 | Construction of Employers office building (RCC framed structure) of minimum floor area of 100 Sqm as per specification and drawings, including all required civil, electrical, plumbing, sanitary works and rain water harvesting structures including fixing of electric fixtures such as fans, tube lights/ LED lamps, furnishing office with minimum furniture for ready occupation of the Engineer including the cost of all material, labour with all lead and lift as per the approved drawing and as directed | 1 | Job | 3200000 |  |  |  |  | 3200000
|  | Grand Total to be Carry forwarded to Schedule No. Pumping Main of Grand Summary for CP 25 | [7 empty] | 19826987.3881

## SOD
Day Works: Bill of Quantities for Day Works for Bytrayanapura Zone
Level | Item No. | Description | Quanitty | Unit | Rate (INR) | Duties | Ex.Work | Local Transport | GST | Total Price (INR)
|  | (1) | (2) |  | (3) |  |  |  |  | (4)=(2) X (3)
2 | 1 | The Contractor is to enter below the fully inclusive rates which he will charge for works carried out on a day work-basis. These rates are to cover for all overtime, subsistence and condition payments, transport of labour, supervisory cost and expenses, overhead charges and profit, waste, fuel, power, water and other consumable stores:use of all hand and pnemuatic tools, light and non-mechanical plant:use of rail tracks, roads, scaffolding, staging, pumps, pipelines, hoists, derricks or cableways erected or in the operation for other purpose and used incidentally: spares and maintanance to plant: all as necessary for the purpose and efficient carrying out of the dayworks ordered. All quantites are provisional.
3 | 1.1 | Labour
4 | 1.1.1 | Unskilled Labour man ( Man Day) | 500 |  | 525 |  |  |  |  | 262500
4 | 1.1.2 | Unskilled Labour woman ( Man Day) | 80 |  | 450 |  |  |  |  | 36000
4 | 1.1.3 | Tradesmen's helper ( Man Day) | 250 |  | 500 |  |  |  |  | 125000
4 | 1.1.4 | Carpenter and jointer ( Man Day) | 25 |  | 1000 |  |  |  |  | 25000
4 | 1.1.5 | Plumber ( Man Day) | 150 |  | 1500 |  |  |  |  | 225000
4 | 1.1.6 | Bricklayer ( Man Day) | 50 |  | 900 |  |  |  |  | 45000
4 | 1.1.7 | Drain Layer and pipe fitter ( Man Day) | 150 |  | 1500 |  |  |  |  | 225000
4 | 1.1.8 | Electrician ( Man Day) | 60 |  | 1300 |  |  |  |  | 78000
4 | 1.1.9 | Fitter ( Man Day) | 130 |  | 1200 |  |  |  |  | 156000
4 | 1.1.10 | Mason ( Man Day) | 75 |  | 950 |  |  |  |  | 71250
4 | 1.1.11 | Bar benders and fixer ( Man Day) | 150 |  | 900 |  |  |  |  | 135000
4 | 1.1.12 | Watchman ( Man Day) | 175 |  | 550 |  |  |  |  | 96250
4 | 1.1.13 | Ganger ( Man Day) | 200 |  | 500 |  |  |  |  | 100000
4 | 1.1.14 | Chainmen and other personnel to assist Engineer's staff ( Man Day) | 60 |  | 2500 |  |  |  |  | 150000
4 | 1.1.15 | Gascutter ( Man Day) | 60 |  | 1200 |  |  |  |  | 72000
4 | 1.1.16 | Welder ( Man Day) | 160 |  | 1200 |  |  |  |  | 192000
0
2 | 1.2 | Materials
3 | 1.2.1 | Diesel engine oil (Litre) | 1300 |  | 200 |  |  |  |  | 260000
3 | 1.2.2 | Welding rods (No) | 2000 |  | 50 |  |  |  |  | 100000
0
2 | 1.3 | Construction Equipment with operation and maintence including operator and required consumables (HOM)
3 | 1.3.1 | Portable compressor with one tool and required length of hose 3 m3/min per hour | 200 |  | 8000 |  |  |  |  | 1600000
3 | 1.3.2 | Mobile crane (10 to 15 tonnes capacity) per hour | 500 |  | 7500 |  |  |  |  | 3750000
3 | 1.3.3 | Dumper / Tipper-5 cum capacity per hour | 400 |  | 8000 |  |  |  |  | 3200000
3 | 1.3.4 | Generating set (33 KVA) per hour | 120 |  | 9000 |  |  |  |  | 1080000
3 | 1.3.5 | Electric welding set including ancillary equipment and consumables per hour | 150 |  | 7000 |  |  |  |  | 1050000
3 | 1.3.6 | -Do- oxy-acetylene gas cutting / gauging per hour | 100 |  | 2500 |  |  |  |  | 250000
3 | 1.3.7 | Loading shovel (1 m3 capacity) per hour | 100 |  | 900 |  |  |  |  | 90000
3 | 1.3.8 | Dewatering pump with required suction hose, foot valve and strainer, delivery hose etc.
4 | (i) | 5 HP (Per day-8 hr shift) | 200 |  | 6500 |  |  |  |  | 1300000
4 | (ii) | 7.5 HP (Per day-8 hr shift) | 200 |  | 9500 |  |  |  |  | 1900000
3 | 1.3.9 | Concrete mixer (0.4/0.3 m3 capacity) per hour | 175 |  | 4100 |  |  |  |  | 717500
|  | Total | [7 empty] | 17291500
Note:
1. This schedule of day works will not be considered for financial evaluation