## Lingadernahalli
BILL OF QUANTITIES
Item No. | Description | Quantity | Unit | Rate in figures (Rs.) | Amount (Rs.)
PART 2A : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - IA : EARTHWORKS
1.1 | Earthwork in excavation of foundation of structures in all types of soil excluding hard rock by mechanical means as per drawing and technical specification, including setting out, providing shoring, strutting and bracing, removal of stumps and other deleterious matter, dressing of sides and bottom, filling back the excavated earth to the extent required and utilising/transporting the remaining earth including coast of labour, materials,lead and HOM of machineries etc., complete as per specifications. | 5155 | Cum | 183 | 943365
1.2 | Earthwork in excavation by manual means for structures in all types of soil excluding hard rock, including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50m after breaking of clods complete as per specifications
a) | 0 to 1.5 m depth | 235 | Cum | 438 | 102930
b) | 1.5 to 3 m depth | 162 | Cum | 438 | 70956
c) | 3 to 4.5 m depth | 1437 | Cum | 438 | 629406
d) | 4.5 to 6 m depth | 120 | Cum | 438 | 52560
1.3 | Excavation for foundation of all structures, either in pits or trenches 1.5 m and above in width, in hard rock by chiselling and / or wedging where blasting is prohibited, including stacking the excavated stuff clear from the edge of excavation with lead upto 50m including cost of explosives, labour, HOM of equipment complete as per specifications
a) | 0 to 1.5 m depth | 100 | Cum | 1093 | 109300
b) | 1.5 to 3 m depth | 100 | Cum | 1093 | 109300
c) | 3 to 4.5 m depth | 100 | Cum | 1093 | 109300
d) | 4.5 to 6 m depth | 398 | Cum | 1093 | 435014
1.4 | Filling available excavated earth (excluding rock ) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts and including cost of all labour complete as per specifications. | 1491 | Cum | 73 | 108843
1.5 | Disposing off the excess excavated earth of all types within the radius of 25 km from the site by vehicle inluding loading, unloading, with all leads, lifts, labour, HOM of machinery etc., complete. | 6756 | Cum | 243 | 1641708
1.6 | Construction of embankment with approved material Gravel/Murrum with all lifts and leads, transporting to site, spreading, grading to required slope in uniform layers of 150mm to meet requirement complete as per specifications and drawings.(which includes cost of gravel / murrum, labour, watering charges & compaction by vibratory roller) | 750 | Cum | 1472 | 1104000
1.7 | Providing and laying grass turfing on the surface of the embankment as per standards and drawings approved by the Engineer around the Ground level reservoir including cost of all labour complete as per specifications. | 700 | sqm | 309 | 216300
1.8 | Dismantling of existing structures like culverts, bridges, retaining walls and other structures comprising of masonary, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary. sorting the dismantled materials, disposal of unserviceable materials, stacking the serviceable material,with all lifts complete as per specifications,
a) | Manual means: Cement concrete grade M-15 & M-20 or as directed | 100 | Cum | 2186 | 218600
b) | Mechanical means: Cement concrete grade M-15 & M-20 or as directed | 100 | Cum | 1458 | 145800
1.9 | Compaction of original ground upto 95% of proctor dry density with maximum of 6 passes of 8 to 10 tonnes power roller including filling in depression occuring during rolling including cost of all labour, HOM of machinery complete as per specifications. | 1310 | sqm | 37 | 48470
1.1 | Clearing and grubbing road land including uprooting rank vegetation, grass, bushes, shrubs, saplings and trees of girth upto 300mm, removal of stumps of trees cut earlier and disposal of unserviceable materials and stacking of serviceable material to be used or aunctioned, including removal and disposal of top organinc soil not exceeding 150mm in thickness complete as per specifications. By manual means.(In area of thorny jungle) | 1200 | sqm | 40 | 48000
| TOTAL CARRIED TO BILL IA SUMMARY |  |  |  | 6093852
PART 2A : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - IIA : CONCRETE AND ALLIED WORKS
2.1 | Providing and laying in position plain cement concrete of mix 1:3:6 with OPC cement content at 220Kgs using 40 mm and down size graded granite metal course aggregates @0.84cum and the fine agregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications.
a) | Chlorine building, valve chambers,PCC filling for level difference,etc. | 137 | Cum | 6755 | 925435
2.2 | Providing and laying in position plain cement concrete of design mix M15 1:2:4 with OPC minimum cement content at 240Kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, shuttering, labour, HOM of machinery, curing complete as per specifications. | 174 | Cum | 6940 | 1207560
2.3 | Providing and laying in position reinforced cement concrete of design mix M25(Minimum cement content of 360kg/m3) as per specifications using 20 mm and down size graded granite metal course aggregates and the fine agregates with superplastisiser conforming to IS9103-1999 reaffirmed-2008, machine mixed, concrete laid in layers not exceeding 15 cms, thick, well compacted, in foundation and plinth , ground floor level for roof slabs, staircase, lintels, etc, including cost of all materials, labour, HOM of machinery, curing complete as per specifications for chlorine house and security cabin,etc. | 402 | Cum | 7912 | 3180624
2.4 | Providing and laying cement concrete in position reinforced cement concrete of design mix M30(Minimum cement content of 400kg/m3) as per specifications by pumping using 20 mm and down size granite Coarse aggregates & fine aggregates of ready mixed concrete (RMC) for R.C.C works laid in 15 cms thick layers and well compacted including vibrating, curing, including smooth finish in CM 1:3, with all lead and lifts etc., complete (exclusive of cost of steel and fabrication charges.) Ready Mixed Concrete for raft foundation, walls, Beams, Columns, underground chambers, baffle walls, Staircase,roof,etc., complete as per specifications. | 3910 | Cum | 8530 | 33352300
2.5 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons.(Type F1 finish)
a) | Reservoir,Chlorine House ,security cabin,etc., | 412 | sqm | 729 | 300348
2.6 | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 4938 | sqm | 729 | 3599802
b) | Level from 3.50 to 4.50m | 1200 | sqm | 729 | 874800
c) | Level from 4.50 to 5.50m | 1200 | sqm | 729 | 874800
d) | Level from 5.50 to 6.50m | 1000 | sqm | 729 | 729000
e) | Level from 6.50 to 14.00m | 5000 | sqm | 729 | 3645000
2.7 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 1827 | sqm | 729 | 1331883
b) | Level from 3.50 to 4.50m | 250 | sqm | 729 | 182250
c) | Level from 4.50 to 5.50m | 250 | sqm | 729 | 182250
d) | Level from 5.50 to 6.50m | 250 | sqm | 729 | 182250
e) | Level from 6.50 to 14.00m | 500 | sqm | 729 | 364500
2.8 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Beams Level from 0.00 to 3.50m | 766 | sqm | 729 | 558414
b) | Beams Level upto 4.50m | 406 | sqm | 729 | 295974
c) | Beams Level upto 14m | 630 | sqm | 729 | 459270
2.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs, landing, balconies and likes thickness upto 200 mm including cost of all materials, labours, complete as per specifications. (Type F2 finish)
a) | Reservoir, Chlorine house,security cabin,etc., | 4626 | sqm | 729 | 3372354
2.1 | Providing TMT bars of Fe 500(CRS) grade steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 503 | MT | 71308 | 35867924
2.11 | Providing TMT bars of Fe500 grade steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 32 | MT | 67665 | 2165280
2.12 | Fabricating and supplying anchor bolts, pipe sleeves, channels, angles, plates and all other types of inserts in concrete members and placing them in position as specified on drawings at all locations and at all levels including two coats of approved oil paint over one coat of zinc-rich primer over exposed surfaces. | 720 | kg | 108 | 77760
2.13 | Filling of box-outs left in RCC walls, etc after erection of pipes, inserts in reinforced concrete of grade M30 with coarse aggregate of size 20 mm downgraded, including roughening and preparing internal surfaces of box-outs, adding expansive agents to concrete, shuttering for Class F2 finish, compacting, curing, finishing etc complete but excluding reinforcement wherever specified.
a) | For M30 grade concrete (Minimum cement content of 400kg/m3) | 270 | Cum | 9511 | 2567970
| TOTAL CARRIED TO BILL IIA SUMMARY |  |  |  | 96297748
PART 2A : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - IIIA : GENERAL BUILDING WORKS
3.1 | Providing and laying 230 mm thick rubble packing in plinth with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, including spreading 12 mm layer of stone grit on top, etc., complete for all building works as per drawings, details and specifications. | 169 | sqm | 713 | 120497
3.2 | Providing and constructing precast concrete solid blocks with compressive strength not less than 35kg. per sqm with cement mortar 1:4 masonry (quoin, Jamb, closer blocks) with solid concrete blocks of size 40X20X20 cms conforming to IS.2185/ 1965 in superstructure including cost of materials, labour charges, double scaffolding, curing complete as per specifications. | 282 | sqm | 1454 | 410028
3.3 | Providing plastering to masonry including providing and removing double scaffolding rounding of all corners whever required smooth rendering curing etc., complete as per specifications with burnt brick masonry plain plastering 20mm thick in CM 1:4 (external) | 1245 | sqm | 336 | 418320
3.4 | Providing plastering to masonry including providing and removing scaffolding rounding of all corners whever required, smooth rendering curing etc complete as per specifications with burnt brick masonry plain plastering 12mm thick in CM 1:4 with lime rendering (internal) | 928 | sqm | 283 | 262624
3.5 | Providing and finishing external walls in two coats with waterproof cement paint and primer of approved brand and shade to give an even shade after throughly brooming the surface to remove all dirt and loose powdered material, free from mortar drops and other foreign matter cost of materials, labour, complete as per specifications.
a) | Reservoir,Chlorine House and watchman cabin,etc., | 3183 | sqm | 175 | 557025
3.6 | Providing and applying painting in two coats with plastic emulsion paint and primer of approved brand on wall surface to give an even approved shade after thoroughly brushing the surface, free from mortor drops and other foreign matter including preparing the surface even and sand paper smooth, cost of materials, labour, complete as per specifications.
a) | Chlorine House and security cabin,etc., | 1836 | sqm | 178 | 326808
3.7 | Providing and laying flooring and steps fine machined polished granite stone slabs of approved colour 20mm thick on cement mortar bed 1:6, 20mm thick, and, joints finished with cement mortar 1:3 over existing cement concrete bed ,including cost of materials, labour, curing complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin,etc. | 137 | sqm | 4372 | 598964
3.8 | Providing and fixing skirting of 300mm high using prepolished water cut/gang saw of 19mm thick grey granite 0.5mm wide chamfered width and depth and fixing in CM 1:4 of 20mm thick after chipping the walls, etc., including cost of all materials, mortar,labour,curing,etc., complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin,etc. | 140 | RM | 1312 | 183680
3.9 | Providing dado, rises of steps with colour glazed tiles on 10mm thick cement plaster 1:3 and jointed with white cement slurry over rough plaster surface ( excluding cost of rough plastered surface which should be measured and paid separately) using glazed tiles of approved make and size including cost of materials, labour, complete as per specifications.
a) | chlorine house, reservoir staircase,etc. | 150 | sqm | 1299 | 194850
3.1 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tiles of approved make and colour of size 100 mm x 200 mm x 20 mm thick for flooring, on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Neutralization pit, walls and base slab | 80 | sqm | 4070 | 325600
3.11 | Providing and laying M-15 cement concrete flooring, 60mm thick with metallic concrete hardner topping, under layer of 45mm thick M-15 cement concrete using broken granite metal of 20mm and downsize and top layer of 15mm thick metallic cement hardner consisting of mix 1:2 by volume, with metallic hardening compound of approved quality mix in the ratio of 4:1, including finishing, cost of materials, labour, curing, complete as per specifications.
a) | Drum room and chlorinator room | 150 | sqm | 886 | 132900
3.12 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tile dado of approved make and colour of size 100 mm x 200 mm x 20 mm thick for on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Drum room and chlorinator room | 38 | sqm | 4070 | 154660
3.13 | Providing and fixing ceramic tiles (non skid) of size 400x400mm for flooring laid on a bed of 20mm thick cement mortar 1:3 mix flush pointing with white cement mixed with matching colour pigment including curing, cleaning,etc., complete.The work includes cost of all materials,mortar,labour charges for all items of work,hire charges for equipment,etc., complete as per specifications.
a) | Wash room of control and Office rooms | 38 | sqm | 1325 | 50350
3.14 | Providing, fabricating and fixing in position anodised aluminum doors using following aluminum sections mat or glossy finish, outer frame of section 101.6 x 44.45 x 3.18 mm at 2.404 Kg/m, door shutters vertical section - 44.62 x 44.45 x 3.00mm at 1.426 Kg/m, bottom section 114.3 x 44.45 x 3.18mm at 2.646 kg/m, top section 47.62 x 44.45 x 3.00mm at 1.426 kg/m, middle section 49.91 x 44.45 x 3.00mm at 1.495 Kg/m, glazing clips 19 x 17.3x 11mm x 0.90 mm thick at 0.124 kg/m, all sections anodised to 12 to 15 microns. Cut to length, joint mitred corners grinded, shutters pivoted opening arrangement with h eavy duty aluminum alloy automatic door closer, floor mounted, providing and fixing standard approved accessories such as aluminum handle, for full width or length, tower bolts, lock pivots, PVC or rubber gaskets with 5.5 mm thick plain glass for top and bottom panel, aluminum sections treated for removal of rust, coated with greasy material for non adherence of mortar or any sticky material, the assembled frame fitted with corner angles, strips and fitted with rawl plugs, or teak wood gutties, to RCC columns, or masonry sides, including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. as per specifications | 42 | sqm | 9472 | 397824
3.15 | Providing, fabricating and fixing in position Stainless steel doors including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. | 6 | sqm | 36429 | 218574
3.16 | Providing and fixing mechanical gear type rolling shutters of approved make out of 18 guage, 75mm wide cold rolled steel laths of convex corrugation, with side guides and bottom rail, with interlocking arrangements for steel laths by means of alternate clips, suspension shaft with High tension coil type springs two numbers, mounted on specially designed pipe shaft, with bracket plates, guide channels, ball bearing arrangements, for inside & outside locking complete including pulling hooks, 4Nos. handles with all fittings and accessories, painted with a coat of red lead paint (without top cover) cost of materials, labour, HOM of machinery complete as per specifications. | 18 | sqm | 7286 | 131148
3.17 | Providing and fixing hydraulic door closures -Aluminium body | 6 | Nos. | 2915 | 17490
3.18 | Providing and fixing mortice door lock heavy duty to doors. | 10 | Nos. | 2186 | 21860
3.19 | Providing and fixing in position anodized aluminium windows and ventilators as per approved drawings with sliding shutters using double track window frame section of size 61.85x31.75mm. with 1.2mm thick, bottom section weight 0.695 kg/m, sides and top sections 1.3 mm. thick weight 0.659 kg/m; and shutter comprising top and bottom section of size 40mmx18mm, 1.25mm thick 0.417 kg./m; shutter outer side 40mmx18mm, 1.25mm.thick weight 0.417 kg/m, shutter interlock section 40mmx26.7mm, 1.1mm thick, weight 0.469 kg/m. the shutters mounted on nylon rollers with approved quality of fixtures such as aluminium handles tower bolts etc.; and providing and fixing 5.5mm. thick plain glass for shutters fitted with rubber beading aluminium sections anodised 12 to 15 microns, including cutting to required length, joints mitred subdividing the frame tenonned and rivetted in the assembled frame stiffened with end clips at corners angles etc., and fixed to the walls, lintels, floor beams/cills as the case may be with necessary steel screws, raul plugs, or teak wood gatties including cutting masonry or concrete and making good the original surface using cement mortar, aluminium sections pretreated for removal of any rust and protection of further rust formation and coated with the greasy materials for non- adhesion of mortar and any other sticky materials, (this coating should be cleaned after installation) including cost of all materials, fixtures, labour and HOM of machinery complete as per specifications. | 50 | sqm | 7286 | 364300
3.2 | Providing, fabricating, assembling and fixing in position aluminium partitions with aluminium section anodized to 12-15 microns using sections in combination of plain, single grove and double grove as per requirements for the frames of overall size 101.6mm x 44.45mm, 3.18mm.thick having section weight, plain sections 2.40kg/m single grove section 2.541kg/m. and double grovesection 2.683 kg/m and bottom 46 kg/m; aluminium louvres of size 77.6mmx27.6mm 1.7mm. thick section weight 0.483kg/m; bottom portions provided with 12mm. thick prelaminated sheet both side of approved colour lamination exterior grade; aluminium sections of mat finish or glossy finish using section, spacing of vertical member shall not exceed 0.6 m. c to c; sections are cut to the required lengths, joints mitered and corners grinded subdividing frames tennoned and rivetted to the frames, the assembled frame should be stiffened with corner angles stripped and fixed with screws, rawl plugs and teak wood gutties to R.C.C.columns or masonry on sides, R.C.C. lintels or beams at top and floor at bottom, including cutting chistling and making good with cement mortar to match the surface, providing and fixing bottom panel filled with the materials to a height of 0.9m. from floor level; and 5.5mm. thick plain glass for middle portion viz., 0.9m. to 2.13 m. and top panel with lower sections, the glass and panels fitted with glazing clips of 19mmx17.3mm. with thickness of 0.9mm. weight 0.124kg/m; aluminium sections pre-treated for removal of any rust and prevention of further rust formation, and coated with greasy materials for non-adherence of mortars or any other sticky materials; vertical members embedded in the flooring by making suitable size holes and fixing with cement mortar, with necessary opening for fixing of doors of standard size including cost of materials, fixtures, labour and HOM of machinery complete. | 17 | sqm | 9472 | 161024
3.21 | Providing and fixing 225 mm wide and minimum 6 mm thick continuous PVC waterstops of approved quality at contraction and expansion joints as per manufacturer's instructions at all levels for Ground level reservoir. | 647 | RM | 365 | 236155
3.22 | Supplying and fixing PVC encapsulated CI rungs to shapes and at locations specified in drawings and specifications for Valve chambers | 50 | kg | 108 | 5400
3.23 | Providing and fixing 10 gauge aluminium sheet to required shape and size with rawl plugs and screws to concrete curbs to cover up expansion joints at roof level, including filling the notch with bitumen as specified in drawing, for Ground level reservoir. | 165 | sqm | 2264 | 373560
3.24 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant Type A) in a groove of size 15 mm x 20 mm deep at contraction joints including forming groove as specified on drawing for Ground level reservoir. | 3900 | RM | 387 | 1509300
3.25 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant type B) in a groove of size 25 mm x 20 mm deep at expansion joints including forming groove as specified on drawing for Ground level reservoir. | 450 | RM | 401 | 180450
3.26 | Providing and fixing in position 25 mm thick sellotex board/filler compound as per standards and approved by the Engineer, of required sizes at expansion joints as specified in drawing for Ground level reservoir. | 9600 | sqm | 328 | 3148800
3.27 | Providing and laying 500 gauge polyethylene sheet of approved make and quality on blinding layer and wherever specified as directed by Engineer, for Ground level reservoir. | 250 | sqm | 62 | 15500
3.28 | Providing and fixing slip-strip (1 mm thick PVC sheet) of approved quality or equivalent at junction between top of wall and bottom of roof slab in two layers as directed by Engineer, for Ground level reservoir. | 250 | sqm | 729 | 182250
3.29 | Providing and laying in position yelahanka tiles of size 125 x 250mm of approved quality and make, over a bed of cement mortar 1:3 with thickness varying from 100mm to 25mm including weather proof course and pointed with cement mortar 1:3 mix with red oxide including curing cost of materials, labour complete as per specifications. | 2350 | sqm | 1403 | 3297050
3.3 | Providing and fixing 150 mm diameter cast iron air ventilators as per design & shape indicated in drawings over roof slab of all reservoirs with mosquito proof jali etc complete. | 175 | Nos. | 6896 | 1206800
3.31 | Installing precast circular hume pipe septic tank suitable for 5 persons capacity conforming to IS 2470, and constructing standard soak pit for the same capacity, including excavation and backfilling of pit, PVC Pipe, filling soakpit with broken bricks, overflow connection precast RC slab and construction of manhole chamber with cover, C.I. vent pipe with cowl and connecting it to incoming and outgoing pipelines etc., complete. | 1 | Nos. | 145713 | 145713
3.32 | Supplying of and application of food grade epoxy painting on the inside surface of GLR headroom, GLR inside staircase and wall face at staircase complete, as per applicable Technical specification clause, including all labour, HOM of equipment, lead, lifts taxes etc., complete, including all surface preparation, testing, Rate shall be inclusive of all materials, tools and plants, testing and inspection etc., complete. | 2300 | sqm | 481 | 1106300
3.33 | Providing and laying M15 grade plain concrete in screed for required level above base slab of reservoir to specified slope with coarse aggregate of size 10mm downgraded including formwork and compacting with a hand rammer,curing,finishing,etc., complete as per specifications. | 180 | Cum | 6871 | 1236780
3.34 | Providing and laying plain cement concrete of design mix M15 with OPC minimum cement content at 240kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers with thickness varying from 150mm to 75mm over 230 mm thick rubble packing with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, etc., complete for plinth protection 1m wide as per drawings, details and specifications. | 100 | RM | 1689 | 168900
| TOTAL CARRIED TO BILL IIIA SUMMARY |  |  |  | 17861484
PART 2A : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - IVA : WATER SUPPLY AND SANITARY WORKS
4.1 | Providing and fixing white vitreous china clay, water closet European type (Pedestal type, P-trap) with black solid plastic seat and lid, CP brass hinges, rubber buffers, 10 litre low level, P.V.C flushing cistern (all are approved make) with fittings, SS brackets, 40mm diameter flush bend with fittings and clamps, overflow arrangements with specials and 25mm mosquito proof coupling of approved design, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 14572 | 29144
4.2 | Providing and fixing white vitreous china clay, flat back wash basins of size 550 mm x 400 mm with a pair of 15mm C.P brass pillar taps with SS brackets, 32mm C.P brass waste of standard pattern, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 8743 | 17486
4.3 | Providing and fixing white vitreous china clay, flat back, lipped front urinal basin of 430x260x350mm in the range of three with 7.5 litres PVC automatic flushing cistern, SS brackets, standard flush pipe and C.P brass spreaders with brass unions and G.I clamps painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 7286 | 14572
4.4 | Providing and fixing in position brass bib cock of aproved quality 15mm nominal bore including cost of all materials, labour and HOM of equipments with all leads complete as per specifications. | 3 | Nos. | 1458 | 4374
4.5 | Providing brick masonry inspection chambers, rectangular in size 90 cm x 45 cm and upto 1.5 m depth on sewer line , with 230 mm brick wall in cement mortar (1:2), plastered both inside and outside with 20 mm thick cement mortar (1:2),including 1.6 m x 1.2 m x 290 mm thick cement concrete 1:2:4 in haunches as per standard plan including excavation, backfilling the excavated sides and removing surplus earth and with heavy duty C.I. cover and frame and with M.S. steps fixed in cement mortar with cement and sand filleting. | 2 | Nos. | 26223 | 52446
4.6 | Same as in for item 4.5 above but for depth greater than 1.5 m and upto 3 m | 2 | Nos. | 38907 | 77814
4.7 | Constructing circular type manhole 1500mm internal dia at bottom, 525mm dia at top, in wire cut burnt brick masonry with 1:5 cement mortar, cement plaster 1:3, finish with a floating coat of neat cement, RCC 1:2:4 top slab using 20mm and downsize granite metal, foundation concrete, M7.5 using 40mm and downsize granite metal and making channels in cement concrete M15 using 20mm and downsize granite metal, neatly finished curing, fixing CI cover complete including external, footrests and 12mm thick cement plaster on the external surface, cost of materials, labour charges, HOM of machineries complete as per specifications. | 2 | Nos. | 75964 | 151928
4.8 | Providing and fixing PVC Nahani trap of approved make conforming to ISI specifications and construction of cistern in M-15 as per directions. (rate inclusive of cost of materials and fixtures and conveyance of materials to work spot). | 3 | Nos. | 875 | 2625
4.9 | Providing stoneware gully trap of approved quality and make fixing in M-15 and plastering with CM 1:3 wherever necessary. (rate includes cost of all materials, fixtures and lead). With 100mm outlet. | 2 | Nos. | 1458 | 2916
4.1 | Providing and fixing 75 mm dia PVC slotted vent cowls conforming to IS 3989 with necessary fixtures and as directed by Engineer. | 2 | Nos. | 729 | 1458
4.11 | Providing and fixing white glazed 'P' trap as per IS 2556 (Part 7) 100 mm dia with SS grating 10 mm thick etc., complete. | 1 | Nos. | 1458 | 1458
4.12 | Providing and fixing cast copper alloy stop valves, polished bright, conforming to and as per IS 781.
a) | 25 mm dia. | 1 | Nos. | 729 | 729
b) | 20 mm dia. | 2 | Nos. | 729 | 1458
c) | 15 mm dia. | 1 | Nos. | 729 | 729
4.13 | Providing and fixing SS towel rail 740mm length, 20mm dia with C.P brackets, fixed to wooden cleats with C.P brass screws including cost of materials, labour complete as per specifications. | 4 | Nos. | 2186 | 8744
4.14 | Providing and fixing best quality SS liquid soap bottle holders of approved make with SS brackets, screws, rawl plugs, etc. complete. | 3 | Nos. | 1458 | 4374
4.15 | Providing and fixing 600x450 bevellead edge mirror of superior glass with 6mm hard board backing and fixed to wooden cleats with C.P screws, washers, including cost of materials, labour complete as per specifications. | 4 | Nos. | 7286 | 29144
4.16 | Providing and fixing white glazed partition walls of size 825 mm x 450 mm x 25 mm as per IS 2556 (Part 6 ) of approved make, properly supported with C.I. brackets, etc. complete. | 2 | Nos. | 2911 | 5822
4.17 | Providing and fixing UPVC water pipes and fittings 'B' class pressure rating of 10kg/cm2 conforming to IS 13592 and IS14735, with all necessary fixtures and bends, including testing the line as specified,etc.,complete.
a) | 25 mm dia. | 100 | RM | 292 | 29200
b) | 20 mm dia. | 25 | RM | 219 | 5475
c) | 15 mm dia. | 10 | RM | 146 | 1460
4.18 | Providing and Fixing PVC soil waste and vent pipes 100 mm diameter - 10kg/cm2 with spun yarn soaked in cement slurry and cement mortar 1:2 including cost of materials, labour, testing complete as per specifications. | 200 | RM | 875 | 175000
4.19 | Providing and fixing PVC pipes of approved make and 150 mm dia - 10kg/cm2 conforming to IS 651, including all necessary fixtures and bends, including excavation, backfilling, testing etc., complete as per specification. | 200 | RM | 1284 | 256800
4.2 | Providing and fixing 100 mm dia - 10kg/cm2 PVC rain water pipes as per IS: 4984 including all fixtures such as brackets, bends etc.as directed by the Engineer. | 765 | RM | 315 | 240975
4.21 | Providing and fixing cast iron bell mouth rain water outlets including MS grating, etc., complete as directed by Engineer.
a) | 100mm Dia. | 90 | Nos. | 1458 | 131220
4.22 | Providing, supplying and fixing rectangular SS manhole covers with chains connecting to the frame of size 1200x900 and 900mm x 600mm of grade 304L for roof slab of reservoir and underground chambers at locations shown in drawing including SS frame etc. complete. | 850 | kg | 583 | 495550
4.23 | Supplying PVC pipes conforming to IS 4985:2000 with latest amendments and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations and cuts of pipes wherever necessary including jointing of PVC and specials with jointing of approved type, with all labour with all lead & lifting. (75mm dia - 10kg/cm2) | 65 | RM | 729 | 47385
| TOTAL CARRIED TO BILL IVA SUMMARY |  |  |  | 1790286
PART 2A : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - VA : STRUCTURAL STEELWORKS
5.1 | Supplying, fabricating, delivering to site, loading, unloading, etc. and erecting structural steel work for the following works, including one shop coat of red oxide zinc chromate primer after fabrication and one coat of the same after erection and two coats of synthetic enamel paint of approved shade, etc. complete as per specifications.
a) | Chlorine house | 350 | kg | 108 | 37800
5.2 | Providing and fixing in position MS ladders as per drawing, including painting etc. complete. | 250 | kg | 117 | 29250
5.3 | Providing and fixing 304- grade Stainless steel handrails of 14 gauge pipe for ramps or staircase are made out of stainless steel hollow pipes, using 50mm dia for verticals @ 1.60mtr c/c are fixed to the rams or steps by drilling with bolts and 100mm dia MS base plates 10mm gauge for fixing of vertical pipes 4 nos anchor bolts & 40mm dia pipes are fixed horizontally for 2 rows top one pipe are fixed with vertical pipes another one are fixed with elbows & 25mm dia pipes are fixed horizontally for 2 rows with elbow top measure @ equal intervals including cutting, welding, bending wherever necessary with suitable caps @ tops, bottoms, corners finishing with mat/shining etc., completeincluding cost and conveyance of all materials, labour for all items of work, HOM of euipment with all lead and lift, loading and unloading, transportation charges and all other incidental charges etc., complete as per specification and directions of the Engineer-in-charge of the work. Ramps or staircase for physically challenged. | 400 | RM | 2889 | 1155600
5.4 | Providing and fixing MS frame with 10 mm thick flats with grating cover with stiffeners for openings as specified in drawing at all locations and levels, including painting, etc., complete. | 2500 | kg | 108 | 270000
| TOTAL CARRIED TO BILL VA SUMMARY |  |  |  | 1492650
PART 2A : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - VIA : ROADWORKS
ROADS & DRAINS
6.1 | Construction of Granular sub-base for 200 mm by providing coarse graded material , spreading in uniform layers on prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density, complete as per clause 401 for Grading-v of MORTH V Specifications. | 240 | Cum | 2851 | 684240
6.2 | Providing, laying, spreading and compacting 150 mm graded stone aggregate to Wet Mix Macadam (WMM) specification including premixing the material with water at OMC in mechanical mix plant carriage of mixed material by tipper to site, laying in uniform layers in sub base/ base course on well prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density. MORTH clause 406 | 150 | Cum | 3078 | 461700
6.3 | Providing and applying Primer Coat with bitumen emulsion using emulsion pressure distributor at the rate of 0.60 kg per sqm on the prepared WMM surface including cleaning of WMM surface and spraying primer using mechanical spray jet as per MORTH V specification clause No. 502 complete in all respects. | 1200 | sqm | 34 | 40800
6.4 | Providing and applying Tack Coat on the prepared WMM surface hot bitumen primed at 1Kg per Sqm heating bitumen in boiler fitted with spray set as per MORTH V specification clause No. 503 complete in all respect. | 1200 | sqm | 57 | 68400
6.5 | Providing and laying Bituminous Macadam 50 mm thick from 100-120TPH hot mix plant using crushed aggregates of specified grading premixed with bituminous binder, transported to site, laid over a previously prepared surface to the required grade, level and alignment and rolled by virbratory roller as per MORTH V specification clauses 505 to achieve the desired compaction complete with all lead and lift and direction of Engineer-in-charge. | 50 | Cum | 10448 | 522400
6.6 | Providing and applying Tack Coat on the prepared BM surface at 0.5Kg / Sqm heating bitumen in boiler fitted with spray set as per specification clause No. 503 of MORTH V complete in all respects. | 1000 | sqm | 28 | 28000
6.7 | Providing and laying Semi Dense Bituminous Concrete(SDBM) 25 mm thick with 100-120 TPH hot mix plant using crushed aggregates of specified grading, premixed with bituminous binder 5.4 to 5.6 per cent of mix and filler, transporting the hot mix to work site, laying with a hydrostatic paver finisher with mechanical control to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause No. 508 complete with all lead and lift, with 60/70 Grade bitumen and direction of Engineer-in-charge. | 25 | Cum | 11361 | 284025
6.8 | Construction of coverd drain 0.3m x 0.45m (inside dimensions) with RCC M20 grade 10cm thick for walls and floor, laid over 10cm thick 1:3:6 PCC bed and covered with M30 grade RCC slab 0f 15cm thick excluding earth work including reinforcement @ 35 kg/rmt and form work complete as per specifications. | 400 | RM | 5724 | 2289600
COMPOUND WALL
6.9 | Earthwork excavation for foundation in all types of soil excluding hard rock including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50 m and disposal of excess excavated earth including all leads and lifts after breaking of clods complete as per specifications.
a) | 0 -1.5m | 1051 | Cum | 152 | 159752
6.10 | Providing and laying in position plain cement concrete of mix M10 with OPC cement @220kgs, with 20mm and down size graded granite metal coarse aggregates @ 0.84cum and fine aggregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms thick, well compacted, in foundation and plinth including cost of all materials, labour, HOM of machinery curing complete as per specifications. | 28 | Cum | 6409 | 179452
6.11 | Filling available excavated earth (excluding rock) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts including cost of labour complete as per specifications. | 56 | Cum | 73 | 4088
6.12 | Providing and laying in position Reinforced Cement Concrete of Grade M25 (Design mix) with 20mm and downsize graded granite metal machine mixed, concrete laid in layers not exceeding 15 cm thick, vibrated for R.C.C. beams, columns of all sizes in foundation, plinth and superstructure ground floor levels of roof slabs, base slab, staircases, lintels, columns including cost of all materials, labour, HOM of machinary, curing, complete as per specifications. | 100 | Cum | 7617 | 761700
6.13 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for foundation, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specifications | 323 | sqm | 729 | 235467
6.14 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per speciications. | 202 | sqm | 729 | 147258
6.15 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications | 67 | sqm | 729 | 48843
6.16 | Providing TMT Steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, tying with binding wire and anchoring to the adjoining members whenever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinary complete as per specifications. (Fe 500 grade confirm to IS 1786). | 13 | MT | 69122 | 898586
6.17 | Providing barbed fixed 12x12 guage drawn into stone pillar or iron pillars including drawing in holes wherever necessary excluding the cost of pillar but including the cost of barbed wire and binding wire etc., complete | 1200 | RM | 132 | 158400
6.18 | M.S Angle | 168 | kg | 108 | 18144
6.19 | Providing and finishing external walls in two coats with waterproof paint with primer of approved brand and shade to give an even shade after thoroughly brooming the surface to remove all dirt and loose powdered material free from mortar drops and other foreign matter cost of materials, labour complete as per specifications | 1200 | sqm | 175 | 210000
6.20 | Supplying and fixing M.S rectangular poles made out of 2 equal angles of 65x65x6 mm welded together and fixed in CC (1:2:4) with 2 nos 16mm dia MS hold fast rods each of length 25cms including cost of all materials cutting,bending,scaffolding wherever necessary,nicely finishing the welded joints with all lead lifts and as per specifications including providing 2 coats of approved quality paint over one coat of shop painting. | 96 | RM | 1337 | 128352
6.21 | Providing chain link fencing 50mm size of 8 guage properly stretched between rectangular poles and fixed with suitable bolts & nuts, the free ends shall be welded to the pole and block pipe at top and bottom as required including cost of all materials, labour, lead and lifts and as per the directions of the Engineer in-charge of work including two coats of approved quality paint over one coat of shop paint. | 500 | sqm | 365 | 182500
6.22 | Providing and fixing MS block pipe of 38mm dia of heavy guage of 14 including removing the bends, cutting the pipe, and fixing pipe in between the two vertical poles (MS rectangular poles) and spot welding the chain linkwith MS block pipe including cost of all materials wastage in cutting, scaffolding wherever necessary with all lead and lift,etc., complete including two coats of approved quality paint over one coat of shop paint. | 96 | RM | 209 | 20064
6.23 | Providing and erecting in position., 2400x600x60 mm thk precast slab panels of M25 grade reinforced cement concrete including reinforcement and formwork with coarse aggregate of size 20mm downgraded with minimum cement content of 320kg/cum. The reinforcement consists of 1 no of 10mm dia loop and round the panel, 5 nos of 8mm dia horizontals and 15 nos of 8mm dia verticals equally spaced. The thickness of the panel shall be 60mm thick at the middle and 70mm thick at the edges for a width of 250mm.The gaps between the panels shall be packed with 1:4 cement mortar and the final surface between the panel and RCC post shall be finished using silicon sealant of approved make, complete as per specification & drawing.
a) | For both side plain finished panels of 2400mm x 600mm size, as shown in the drawings. | 96 | Nos. | 3524 | 338304
b) | For one side plain and other side with horizontal grooves as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 96 | Nos. | 3524 | 338304
c) | For one side plain and other side with vertical grooves as as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 96 | Nos. | 3524 | 338304
d) | For one side plain and other side with BWSSB logo as per the pattern panels of 2400mm x 600mm size, as shown in the drawings. | 96 | Nos. | 3524 | 338304
6.24 | Providing and fixing gates consisting of 40 mm NB light glass GI pipes external framework and 8 x 30 MS flats internal framework with 16 guage MS jointing plates and tack welded over the framework with necessary hinges and locking arrangement, including painting over approved primer coat, etc. all complete as per specifications and drawings. | 2 | MT | 107603 | 215206
| TOTAL CARRIED TO BILL VIA SUMMARY |  |  |  | 9100193
PART 2A : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - VIIA : PIPEWORKS, VALVES AND SPECIALS
Pipelines, Specials and Appurtenances
7.1 | Providing, Fabricating, shop welding, transporting, handling, aligning, laying and jointing / welding of MS pipes of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate also include loading and unloading, radiography of joints as specified and hydraulic testing of pipeline to specified pressure as per specifications and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings.
a) | 1200 mm internal diameter with 8 mm shell thickness Overflow Pipe of GLR | 30 | RM | 18597 | 557910
b) | 1000 mm internal diameter with 7 mm shell thickness inlet and outlet pipes | 40 | RM | 13565 | 542600
7.2 | Providing, fabricating, shop welding, handling, transporting, aligning, laying and jointing of MS specials of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate include loading and unloading, radiography of joints as specified and hydraulic testing of specials to specified pressure and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings. | 1100 | kg | 139 | 152900
7.3 | Providing guniting (CM 1:3 over 50 x 50 mm weld mesh of 13 gauge) on the external surface of pipes and specials including supplying and fixing reinforcement as per specifications after cleaning the pipes including curing etc., at fabrication yard and guniting the field joints at site between two pipes after testing complete in all respects as per specifications.
a) | 1217 mm OD pipes and specials, 25 mm thick guniting | 115 | Sq.m | 729 | 83835
b) | 1015 mm OD pipes and specials, 25 mm thick guniting | 128 | Sq.m | 729 | 93312
7.4 | Providing food grade internal epoxy lining of 0.5 mm thick as per specifications to the internal surfaces of mild steel pipeline, fittings, specials etc., including surface preparation, machine lining, curing and testing / inspection etc., complete.
a) | 1200 mm ID pipes & specials to 1200 mm finished diameter, 0.5 mm thick internal epoxy lining | 113 | sqm | 583 | 65879
b) | 1000 mm ID pipes & specials to 1000 mm finished diameter, 0.5 mm thick internal epoxy lining | 126 | sqm | 583 | 73458
7.5 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Manually operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 1000 mm dia PN 16 for 1000 mm ID | 2 | Nos. | 1142166 | 2284332
7.6 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Motorised operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 1000 mm dia PN 16 for 1000 mm ID | 4 | Nos. | 1334649 | 5338596
7.7 | Supply,installation, testing & Commissioning of (Scour purpose) Ductile Iron (DI) Resilient seated soft sealing sluice valve. Detailed Valve specifications & arrangement shall be as defined in Volume 2. The rate is inclusive of cost of mating flanges, valve,bolts & nuts and rubber insertions,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 300 mm dia. PN 16 size scour valves for GLR | 2 | Nos. | 55047 | 110094
7.8 | Providing, supplying and fixing SS 304 Expansion Bellows with Flange Ends as per specifications and drawings.Detailed Specifications & arrangement shall be as defined in Volume 2. The rate shall include transportation to site with all leads and lifts, aligning and jointing approved anti-corrosive paint etc., complete in all aspects. Rates are incluisve of Labour Charges.
a) | 1000 mm dia. PN 16 | 6 | Nos. | 185128 | 1110768
7.9 | Providing and laying following dia of MS pipes conforming to IS 3589 in trenches outside the pipeline scour valve chambers for draining, include lining & coating, excavation, connecting to scour valve, backfilling the earth etc., complete.
a) | 300 mm dia. 5.6 mm thick | 60 | RM | 3294 | 197640
| TOTAL CARRIED TO BILL VIIA SUMMARY |  |  |  | 10611324
PART 2A : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - VIIIA : MECHANICAL WORKS
8.1 | Mechanical Equipment
a) | Supply,Testing, Installation & Commissioing of 8 Kg/hr Capacity with 0-2 ppm dosage level Vaccum type Chlorination System 2 sets.(1W+1S) with all allied works complete as per Bid specification of Volume 2
(i) | 8 Kg/hr | 2 | Sets. | 1635618 | 3271236
b) | Supplying,Testing, Installation & Commissioing of Chlorine gas Filled Chlorine Tonners of 900 Kgs with all allied works complete as per Bid specification of Volume 2 | 4 | Nos. | 189426 | 757704
c) | Supply,Testing, Installation & Commissioing of Electrically operated wire rope hoist of 2 Ton capacity conforming to IS 3938 for chlorine house with suitable I-Beam arrangement and Electrical Panels etc.with all allied works complete as per Bid specification of Volume 2 | 1 | Nos. | 291461 | 291461
d) | Service Water Network system
(i) | Providing, erecting and giving test of Centrifugal Monoblock Pump set conforming to IS 9079 operating at 1500 RPM with pump casing: Cast Iron IS 210 FG Gr.260, Impeller:Bronze IS 318 LTB2, Shaft:SS 410 , Pump Seal: Mechanical Seal, priming funnel, cock, suitable flanges at suction and delivery side. Pump shall have common shaft for pump and motor. Motor shall be suitable for working on 2.0 HP, 415 V + 10%, 3 Ph, 50Hz+/-5% A.C. Supply. Motor shall be TEFC type. Pump set shall be suitable for working at various discharge and head requirements. Pump shall be erected on Provided C.C. foundation block with suitable foundation bolts grouted in C.C foundation block. | 2 | Nos. | 56935 | 113870
(ii) | Pressure Gauge: Supply, delivery at site and fixing of glycerine filled stainless steel pressure gauge of 100 mm Dia. suitable for the above pump sets with nipple, stop cock and three way cock for cleaning and necessary length of SS tubing suitable for mounting on the suction and delivery of pump, including 15 NB isolating valve etc., complete with all lead and lifts etc, complete as per specification | 2 | Nos. | 1909 | 3818
(iii) | Providing and fixing in position brass gate valve with CI wheel (screwed end) 40 mm nominal bore including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 6 | Nos. | 8109 | 48654
(iv) | Providing and fixing in position 40 mm nominal bore non-return valve vertical type of approved make including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 2 | Nos. | 8960 | 17920
(v) | Providing & Fixing to wall,ceiling and floor high density polyethylene pipes 6.00 Kgf/sq.cm working pressure of outside diameter raising mains & exposed distribution pipes with special flange, compression type fittings, wall clips, making good the wall, ceiling and floor, including cost of all materials, labour charges, HOM and testing complete as per specifications.
i | 40 mm dia | 100 | RM | 219 | 21900
(vi) | Providing and placing on terrace,polyethylene water storage tanks with manhole lid and suitable locking arrangements,making holes of suitable diameter for inlet,outlet and overflow pipes,including cost of all materials,labour transportation charges,HOM of equipments and testing complete as per specifications (for 1000 litres capacity) within the GLR Campus. | 1 | Nos. | 14572 | 14572
| TOTAL CARRIED TO BILL VIIIA SUMMARY |  |  |  | 4541135
PART 2A : INSTRUMENTATION WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - IXA : INSTRUMENTATION WORKS
9.1 | ICA Items for City reserviors
a) | Designing, Supplying, Installing, commissioning & testing of Ultrasonic level transmitter with following technical parameters at GLR and Interfacing with PLC panel including all required Mounting accessories, factory testing & inspection complete as per specifications. Range : (0 - 10 m) | 2 | Nos. | 62344 | 124688
b) | Supply, delivery at site and fixing of Conductivity type Level Switch (back up to level transmitter), High Level & Low Level sensing - (4point contact) with necessary instrumentation cabling,glands with suitable stub and flange and bolting arrangement for hook-up, as applicable and necessary, factory testing & inspection. Range : (0 - 10 m) | 2 | Nos. | 78049 | 156098
c) | Design, Supply, Installation, Testing of Residual chlorine analyzer at GLR and Interfacing with PLC panel and factory testing for complete functional test & inspection. | 1 | Nos. | 227160 | 227160
9.2 | Instrument & power supply cables, supplies, laying, termination & testing.
a) | Plain annealed multistranded tinned copper conductors; solid polyethylene insulation with each pair screened with aluminium-mylar tape including drain wire, with collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (2 Pair x 1.5 sq.mm) | 200 | RM | 782 | 156400
b) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (12 Core x 1.5 sq.mm) | 200 | RM | 1434 | 286800
c) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (4 Core x 1.5 sq.mm) | 300 | RM | 1141 | 342300
d) | Conduits and Supports (19mm OD Heavy Mechanical Stress PVC Conduit (Socketed) + Round Elbow + Circular Box (Through,Tee,Intersection,etc) + Coupler (Pipe to Pipe, End Cap) | 1 | Lot | 71627 | 71627
| TOTAL CARRIED TO BILL IXA SUMMARY |  |  |  | 1365073
PART 2A : ELECTRICAL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - XA: ELECTRICAL WORKS
LT Electrical Works for GLR Premises
10.1 | Supplying and erecting four pole metal clad ON LOAD change over switch 415V, 125A erected on angle iron /GI frame approved make complete. | 1 | No. | 10257 | 10257
10.2 | Supply, Transportation, loading/unloading, Laying, Installation & Commissioning of Solid Aluminum conductor up to 10 sqmm balance stranded conductor, XLPE Insulated, cores laid up, PVC tape/Extruded Innersheathed for Multicore Cables , Armour (Aluminium wire for single core up to 70 sqmm balance Aluminium strip, Glavanised wire for cables upto 2x10 sqmm, 3x10 sqmm,4x6 sqmm balance all galvanised steel strip), extruded PVC Type ST2 sheathed, 650/1100V grade as per IS 7098(Part 1) 1988, Incoming Cable from nearst 415V overhead line as per ESCOM specifications a) Metering Box to Change Over Switch b) Change Over Switch to 415V Panel Board
a) | 3.5C x 50sq.mm (Al. Conductor) | 70 | Mtr. | 263 | 18410
b) | 3.5C x 50sq.mm (Al. Conductor) - Glands | 4 | No. | 98 | 392
c) | 3.5C x 50sq.mm (Al. Conductor) - Lugs | 16 | No. | 50 | 800
10.3 | 415V PMCC Panel Board (Including Chlorine MCC): Supply, Transportation, Installation, Testing & Commissioning of 415V LT Board of cubicle type with 415V, 50 Hz, 3 PH, TPN, 25 kA for 1 sec, wtih IP-54 enclosure with Bottom entry, consisting of incoming and outgoing feeders with metering and protection with complete accessories as per specification and single line diagram.
a) | Incomer: 125A, 25kA, 4P, MCCB | 1 | No. | 10850 | 10850
b) | Outgoing: 25A TPN MPCB (Motorised Valves) | 4 | No. | 4307 | 17228
c) | Outgoing: 63A TPN MCCB (Indoor Lighting DB 1 & 2, Spare 2Nos.) | 4 | No. | 9074 | 36296
d) | Outgoing: 32A TPN MCCB (2T Crane, Spare 2Nos.) | 3 | No. | 7112 | 21336
e) | Supplying & erecting LED type indicating pilot lamp with LED colours red , yellow and blue, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 1 | Set | 1697 | 1697
f) | Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 32 | No. | 566 | 18112
g) | Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod upto 250A MCCB | 8 | No. | 1465 | 11720
h) | Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 100/5A, 5 VA , class 1 accuracy | 3 | No. | 625 | 1875
i) | Multi Functions Meters - Flush type for M V Panel Board LED type, CT/PT, Voltage, Current, Frequency, Kilowatt, Kilo Volt Ampere, KVAR , KVAH, Run Hours, unbalance(V,A),Rpm, Phase angles,Thd-Class 1 With RS 485 Port | 1 | No. | 10390 | 10390
j) | Supplying, erecting & marking SPMCB 5A in provided distribution board | 3 | No. | 571 | 1713
k) | DOL Feeder a) 25A MPCB - 1No b) Supplying and erecting D.O.L. Starter 400V. 3 phase, 50 cycles with no volt coil and overload element with necessary materials and connected to supply upto 7.5 H.P. - 1No. c)Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. d) Supplying, fixing and wiring 0 to 30amps Ammeter Analog SR 65 5D/5A C.T.operated-AC - 1No. e) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 30/5A, 5 VA , class 1 accuracy - 1No. | 8 | No. | 8943 | 71544
l) | Push button station / Local Control Panel near Pump a) Push Buttons (Start & Stop including emergency Stop). - 3Nos. b) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. c) The cost for fabrication panel, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 8 | No. | 3010 | 24080
m) | Supply and fixing of Electrolytic grade copper bus bar bus bar by means of SMC / DMC type insulator, high tensile nuts and bolts spring washers in existing panel including bending , cutting in required shape and size and colour coding with heat shrinkable PVC sleeves | 28 | Kg | 987 | 27636
n) | 415V PMCC Panel Board Fabrication with enclosures, earthing bus, wiring, control relays, Auxiliary contactors, Control Transformers, power contactors, Control MCBs, terminal blocks etc. All complete works. | 1 | Set | 86961 | 86961
10.4 | Indoor Lighting DB: Supply, Transportation, Installation, testing & Commissioning of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos DP outgoings and for 1 No 4 pole Incomer with IP-54 enclosure, bottom entry cable, necessary accessories like wiring, contactors, terminal block, aux. relays, timer etc complete. a) Incomer: 63A, TPN, MCCB and 100mA, RCCB b) Outgoings: 6-32A, DP, MCB - 8 Nos and 32A TPN MCB - 3Nos c) Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod 63A MCCB - 1No. d) Supplying, erecting & marking SPMCB 5A in provided distribution board - 3Nos. e) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. - 6Nos. f) Supplying and erecting panel mounting type digital ammeter having three and half digit LED display, external CT operated, calibrated for suitable to operate on 500V, 0 to 1000A AC supply with necessary PVC wire leads and lugs and mounting hardware on provided panel complete with calibration certificate from manufacturer.. - 1No. g) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 60/5A, 5 VA , class 1 accuracy.- 3Nos. | 2 | No. | 41716 | 83432
a) | The cost for fabrication panel, Copper / Al busbars, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 2 | Set | 14601 | 29202
10.5 | Outdoor Lighting DB
a) | Supply of Way TPN DB Horizontal with IP 43 Protection suitable for 6DP out goings and for 1 No 4 pole Incommer etc complete as per IS 8623; IS 13032; IEC 61439-3. | 2 | No. | 1527 | 3054
b) | Supplying, erecting & marking DPMCB 16A B- series (for lighting) in provided distribution board | 8 | No. | 1068 | 8544
c) | Supplying, erecting & marking TPNMCB 32A in provided distribution board | 2 | No. | 2014 | 4028
10.6 | Lighting system (indoor and outdoor):
a) | Supply of Lighting Luminiares
i) | Supply, transportation and fixing of 36W Recessed / Surface mounting 2' x 2' (600x600 mm) LED luminaire made of CRCA sheet housing with powder coated with acrylic diffuser, Constant current Driver as per IS: 15885 (Part 2/ Sec 13) : 2012, With System lumen output ≥3200lm operating voltage range of 150 to 265 Volts AC, P.F > 0.9, Surge protection: 2KV, THD<10%, with high power LED's having efficacy of > 120 lumins / watt, CCT: 3000K - 5700K, minimum CRI>70, .etc.,, complete. | 26 | No. | 4761 | 123786
ii) | Emergency Lighting: Supply & Fixing of Rechargeable emergency lamp (600 mm fluorescent lamp) or LED lamp with accessories complete | 4 | No. | 2703 | 10812
b) | Fixing all types and all capacities of LED fittings on the wall / ceiling / rafters / girders using 23 / 0.0076” twin twisted PVC insulated wires, required Nos of round blocks and clamps. | 13 | No. | 216 | 2808
c) | Supply and transportation of LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 110 lm/W and junction temprature < 70°C, with Ingrees protection IP66, Luminaire performance complies to IS 10322 (Part 5 / Sec-3), Driver surge protection 4KV, external Surge protection 10 KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete
i) | 150W | 3 | No. | 11262 | 33786
ii) | 60W | 10 | No. | 5018 | 50180
d) | Supplying and erecting street light / Peripheral light bracket for erection of single fitting made from 40 mm. dia ‗B‘ class G.I. pipe 1.0 m in length along with pole cap of 300 mm length 100 mm dia duly welded | 10 | No. | 765 | 7650
e) | Fabrication, Transportation and supply of hot-dip galvanized Octogonal Pole with BSEN - 10025 grade S 355 JO steel plate for shaft, IS 2062 for base plate with door opening arrangement, including the supply of suitable boards with bakelite sheet as per IS specification suitable to withstand the wind speed of 180 KMPH for 7.5 Mtrs height Pole having dimensions Bottom 130 mm,. Top 70mm with 3mm thick, base plate 220 x 220 x 12mm and 4 Nos of M20 x 700 long 'J' bolts along with template. | 3 | No. | 11225 | 33675
f) | Fabrication, Transportation and supply of 1 / 1.50 Mtr Length Single Arm Bracket made with MS galvanized 40mm / 50mm dia Pipe. (Pole Brackets) | 3 | No. | 1934 | 5802
g) | Foundation and erection charges with special T&P, for 7.5 Mtrs long Octagonal duly erecting on base plate duly providing 4 Nos foundation bolts with nuts with providing of 0.45Mtr x 0.45Mtrs x1.20 Mtr size M20 cc work vibrated concreting mixing with necessary steel (10kgs) reinforcement and curing for 7 days as directed by the field engineers during execution including excavation of Earth/BT all labour charges and cost and conveyance of materials etc.complete. | 3 | No. | 8302 | 24906
h) | Supply of following sizes thermo plastic cable junctions boxes IP 65 protection with metric knockouts for cable entry including threaded cable gland. (260X210X116) | 3 | No. | 1557 | 4671
10.7 | Supply & Installation of Earthing system
a) | Providing earth electrode of low carbon steel rod, UL listed of 17.2 mm dia, 3 Mtr long, coated with copper of 254 microns thickness, CPRI tested for short time current withstand test of 25 kA, coating thickness, environmental test (Salt Mist Test), Bend test, Tensile strength, Yield / tensile ratio, Electrical Resistivity test, complete with clamps and 2 bags of Earthplus ULTRA high grade earthing compound IEC 62561-7 complaint Eco-friendly, Maintenance free, anti corrosive, lead-free, super conductive, mineral based high-grade earthing compound, to enhance soil conductivity. With resistance <0.20 ohmsmeter, should be leach proof & sulphur free complete with earth inspection chamber of dimensions : Width : 320 mm x 320 mm, Height : 192 mm, Weight : 30 Kgs, Load bearing capacity :5000 Kgs | 4 | No. | 9489 | 37956
b) | Supplying and running of GI strips & GI wire for grounding connections, using necessary fixing materials as required.
i) | 32x6 mm GI Earth Strip (For 415V PMCC & Outdoor Lighting Circuit) | 300 | Mtr. | 160 | 48000
ii) | 25x6 mm GI Earth Strip (for Lighting panel & LDB) | 150 | Mtr. | 116 | 17400
iii) | 8 SWG GI Wire (Junction box, Motorised valves etc.) | 200 | Mtr. | 19 | 3800
10.8 | Supply & Installation of Lightning Protection System
a) | Supply of Standard / Special Mounting Structure of height 4.5 mts. pipe, and 300 x 300 x 8mm MS plate, 3 mts. 48mm OD class C GI outer pipe,1.8 mtr, 38mm OD inner pipe, for roof mounting on concrete base and with FRP adapter | 1 | No. | 18777 | 18777
b) | Supply and run of 25mm x 6mm GI Flat Down Condutor with necessary clamps / supports on wall / floor / ground for earth connection | 120 | Mtr. | 116 | 13920
c) | Supply of Test Link Box for each Down conductor in order to disconnect the earth termination system to enable measurement of resistance | 1 | No. | 4620 | 4620
d) | Supply and insallation maintenance free Gl Earthing System comprising of 50mm dia and 2 mtr. long earth electrode of low carbon steel rod with 100 micron bonding and 25 kgs. of carbon based environment friendly backfill compound and suitable clamp | 1 | No. | 8530 | 8530
10.9 | Point Wiring for lighting/fan circuits & sockets
a) | Supply of ISI marked 40mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe | 100 | Mtr. | 88 | 8800
b) | Supplying and erecting unbreakable concealed type modular switch box with double mounting plate for 6 module duly erected flush to wall with required chiselling and finishing with cement mortar / POP as per required to match the background. | 10 | No. | 190 | 1900
c) | Supply of ISI marked 25mm / 32mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe.
i) | Short point (not exceeding 3m) | 30 | Mtr. | 77 | 2310
ii) | Medium point above 3m and up to 6m | 50 | Mtr. | 77 | 3850
iii) | Long point above 6m and up to 10m | 35 | Mtr. | 77 | 2695
d) | Supply of 4 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 80 | Mtr. | 38 | 3040
e) | Supply of 2.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 380 | Mtr. | 27 | 10260
f) | Supply of 1.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 170 | Mtr. | 18 | 3060
g) | Supply & Fixing of modular switch & connected accessories on existing switch plate and enclosure
i) | 32A TPN MCB + 40A TPN RCCB (socket-Industrial Type) | 2 | No. | 8305 | 16610
ii) | One/Two way piano type switch 6A | 20 | No. | 92 | 1840
iii) | 3 pin plug socket 6A | 15 | No. | 139 | 2085
iv) | Piano type switch 16A | 2 | No. | 213 | 426
v) | 3 pin plug socket 16A | 2 | No. | 152 | 304
h) | Supplying and erecting five star rated energy saving Ceiling fan 230 V A.C. 50 cycles 1200 mm complete erected in position | 2 | No. | 3091 | 6182
10.1 | Supply, Installation, Testing and commissioning of safety procedures for Electrical Equipments as per scope, specification and drawings.
a) | Supplying and Fixing PVC synthetic elastomer electrically insulating mat with class D insulation conforming to IS:15652-2006 and CPRI tested upto 11kV | 2 | No. | 6086 | 12172
b) | Supplying and Erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg capacity cartridge type conform to IS 2876/15683 complete erected with necessary clamp made of 50x6 mm M.S. flat nut and bolts grouted in wall complete | 3 | No. | 11252 | 33756
c) | Supplying rubber gloves of 15KV conforming to IS for electrical purpose. | 2 | pairs | 1294 | 2588
d) | Supplying standard first aid box with necessary antiseptic cream, medicine for use on wounds due burn, crepe bandage, gauge bandage, medicated ready to use bandage (Band-Aid) adhesive tape for medicinal use, scissors, anti-septic solution, etc. (All above contents shall be of standard makes) | 1 | No. | 917 | 917
e) | Supplying and fixing of shock treatment chart on the wall with inside plastic sheet cover and plywood back plate frame work complete | 2 | No. | 774 | 1548
f) | Supplying and fixing of danger board made out of MS sheet metal with duly painted with red oxide and enamel paint. | 2 | No. | 129 | 258
g) | Tools and Plant
i) | Live Line Tester | 5 | No. | 92 | 460
ii) | Insulation Tester (Megger) 2.5kV-5kV | 1 | No. | 5911 | 5911
iii) | Multimeter electronic type | 2 | No. | 1183 | 2366
iv) | Earth Resistance Tester | 2 | No. | 7092 | 14184
v) | Rubber Shoes Knee Height | 3 | No. | 629 | 1887
vi) | DC Voltmeter range - 3V to +5V | 3 | No. | 591 | 1773
| TOTAL CARRIED TO BILL XA SUMMARY |  |  |  | 1091818
PART 2A : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
BILL OF QUANTITIES - XIA : MISCELLANEOUS WORKS
11.1 | Supply, delivery at site and fixing of Electromagnetic Flow Indicating Transmitter (full bore type) with flange Ends, rates shall be inclusive of mating flanges with necessary fasteners and gaskets, as applicable and necessary.
a) | Inlet of the reservoir, pipe size 1000 mm | 1 | Nos. | 536541 | 536541
11.2 | Miscellaneous Instruments
a) | Designing.supplying, Installing commissioning & testing of Surge Protection Devices | 6 | Nos. | 32558 | 195348
b) | Designing,supplying, Installing commissioning & testing of online UPS with AC Distribution Board(Min 5 KvA Industrial UPS with 60 min backup on full load of field instrumentation and control equipment inclusive of communication equipment to transfer data to CSC) and factory testing & inspection. | 1 | Nos. | 14650 | 14650
c) | supplying, Installing commissioning & testing of Junction Boxes | 4 | Nos. | 18279 | 73116
d) | supplying, Installing commissioning & testing of Field Instrument enclosures-IP 65 rated for all field instruments. | 7 | Nos. | 8954 | 62678
11.3 | Automation System
a) | Designing.supplying, Installing commissioning & testing of hot standby PLC with 16" colour HMI to control valves and to monitor the level and flow in the facility with required SCADA software.HMI shall be color with touchscreen functionality for complete auto operationm with FAT & SAT as per Contract requirements.(also include integration of flowmeter data (flowmeter’s which has been installed under other contracts) with the PLC based control system for continuous monitoring of both incoming and outgoing flow data at each location. All required cabling for connection, required hardware (splitters) with the PLC based control system shall be integral part of scope of work under this contract) | 1 | No. | 1074393 | 1074393
b) | Designing, supplying, installing, commissioning & testing of CCTV IR water proof camera suitable for upto 100ft.with IR Dome camera, control key board, DVR, Hard Disk, cables, UPT transreceivers etc. complete. (Close Circuit Television System to be installed at the reservoir locations to cover all areas of the facilities) and factory testing & SAT. | 4 | No. | 26866 | 107464
Electrical
11.4 | LT Cables
a) | Supplying, Erection & Termination of XLPE armoured cable copper conductor continuous 5.48 sq.mm. (12 SWG) GI earth wire complete erected with glands & lugs, on wall/trusses/pole or laid in provided trench/pipe as er PWD specifications.
(i) | 4C x 6 Sq.mm (LDBs, Recepacle, EOT Crane, etc.,) | 240 | Mtr. | 280 | 67200
(ii) | 4C x 4 Sq.mm (Street Lighting) | 70 | Mtr. | 209 | 14630
(iii) | 3C x 4 Sq.mm (Pumps, Valves motors, Lighting ckts, 1-ph sockets etc.,) | 870 | Mtr. | 171 | 148770
(iv) | 3C x 2.5 Sq.mm (Outdoor Peripheral light and Indoor Exhaust Fans) | 430 | Mtr. | 135 | 58050
(v) | 1 core x 2.5 sqmm, Cu. Conductor (for protective earth) | 180 | Mtr. | 7 | 1260
11.5 | Cable tray
a) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 300 mm width & 100 mm height comprising all required standard accessories. | 16 | Mtr. | 442 | 7072
b) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 150 mm width & 100 mm height comprising all required standard accessories. | 150 | Mtr. | 354 | 53100
11.6 | Hume pipe for Road crossings for Cable & Earth Strip crossing
a) | RCC Hume Pipe, 2000 mm Long, 150 mm Dia | 8 | No. | 223 | 1784
b) | Collars for RCC Hume Pipe | 4 | No. | 60 | 240
c) | Laying of RCC Hume pipes | 8 | No. | 33 | 264
11.7 | MS Chequrred plate of 6mm thick and 5.sq.meter area for trenches. | 250 | Kg | 110 | 27500
11.8 | Supplying and erecting exhaust fan heavy duty 440 V A.C. 50 cycles 900 RPM 375/380 mm complete erected in position. | 1 | No. | 4098 | 4098
| TOTAL CARRIED TO BILL XIA SUMMARY |  |  |  | 2448158

## Summary - Lingadernahalli
CONTRACT NO. CP-13
Part 2A : CIVIL AND ELECTRO MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT LINGADERNAHALLI
SUMMARY OF BILL TOTALS
Bill No. |  | Amount in Rs.
IA | Earthworks | 6093852
IIA | Concrete and Allied works | 96297748
IIIA | General Building Works | 17861484
IVA | Water Supply & Sanitary Works | 1790286
VA | Structural Steel Works | 1492650
VIA | Roadworks | 9100193
VIIA | Pipeworks, Valves and Specials | 10611324
VIIIA | Mechanical works | 4541135
IXA | Instrumentation works | 1365073
XA | Electrical works | 1091818
XIA | Miscellaneous works | 2448158
TOTAL CARRIED TO GRAND SUMMARY |  | 152693721

## Singapura
BILL OF QUANTITIES
Item No. | Description | Quantity | Unit | Rate in figures (Rs.) | Rate in words (Rs.) | Amount (Rs.)
PART 2B : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - IB : EARTHWORKS
1.1 | Earthwork in excavation of foundation of structures in all types of soil excluding hard rock by mechanical means as per drawing and technical specification, including setting out, providing shoring, strutting and bracing, removal of stumps and other deleterious matter, dressing of sides and bottom, filling back the excavated earth to the extent required and utilising/transporting the remaining earth including coast of labour, materials,lead and HOM of machineries etc., complete as per specifications. | 3650 | Cum | 474 | #NAME? | 1730100
1.2 | Earthwork in excavation by manual means for structures in all types of soil excluding hard rock, including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50m after breaking of clods complete as per specifications
a) | 0 to 1.5 m depth | 546 | Cum | 438 | #NAME? | 239148
b) | 1.5 to 3 m depth | 235 | Cum | 438 | #NAME? | 102930
c) | 3 to 4.5 m depth | 2550 | Cum | 438 | #NAME? | 1116900
d) | 4.5 to 6 m depth | 100 | Cum | 438 | #NAME? | 43800
1.3 | Excavation for foundation of all structures, either in pits or trenches 1.5 m and above in width, in hard rock by chiselling and / or wedging where blasting is prohibited, including stacking the excavated stuff clear from the edge of excavation with lead upto 50m including cost of explosives, labour, HOM of equipment complete as per specifications
a) | 0 to 1.5 m depth | 10950 | Cum | 1093 | #NAME? | 11968350
b) | 1.5 to 3 m depth | 10950 | Cum | 1093 | #NAME? | 11968350
c) | 3 to 4.5 m depth | 10950 | Cum | 1093 | #NAME? | 11968350
d) | 4.5 to 6 m depth | 100 | Cum | 1093 | #NAME? | 109300
1.4 | Filling available excavated earth (excluding rock ) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts and including cost of all labour complete as per specifications. | 24982 | Cum | 73 | #NAME? | 1823686
1.5 | Disposing off the excess excavated earth of all types within the radius of 25 km from the site by vehicle inluding loading, unloading, with all leads, lifts, labour, HOM of machinery etc., complete. | 14647 | Cum | 243 | #NAME? | 3559221
1.6 | Construction of embankment with approved material Gravel/Murrum with all lifts and leads, transporting to site, spreading, grading to required slope in uniform layers of 150mm to meet requirement complete as per specifications and drawings.(which includes cost of gravel / murrum, labour, watering charges & compaction by vibratory roller) | 3120 | Cum | 1472 | #NAME? | 4592640
1.7 | Providing and laying grass turfing on the surface of the embankment as per standards and drawings approved by the Engineer around the Ground level reservoir including cost of all labour complete as per specifications. | 1914 | sqm | 309 | #NAME? | 591426
1.8 | Dismantling of existing structures like culverts, bridges, retaining walls and other structures comprising of masonary, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary. sorting the dismantled materials, disposal of unserviceable materials, stacking the serviceable material,with all lifts complete as per specifications,
a) | Manual means: Cement concrete grade M-15 & M-20 or as directed | 100 | Cum | 2186 | #NAME? | 218600
b) | Mechanical means: Cement concrete grade M-15 & M-20 or as directed | 100 | Cum | 1458 | #NAME? | 145800
1.9 | Compaction of original ground upto 95% of proctor dry density with maximum of 6 passes of 8 to 10 tonnes power roller including filling in depression occuring during rolling including cost of all labour, HOM of machinery complete as per specifications. | 4769 | sqm | 37 | #NAME? | 176453
1.1 | Clearing and grubbing road land including uprooting rank vegetation, grass, bushes, shrubs, saplings and trees of girth upto 300mm, removal of stumps of trees cut earlier and disposal of unserviceable materials and stacking of serviceable material to be used or aunctioned, including removal and disposal of top organinc soil not exceeding 150mm in thickness complete as per specifications. By manual means.(In area of thorny jungle) | 10350 | sqm | 40 | #NAME? | 414000
1.11 | Cutting of trees girth from 300mm to 600mm including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in the depressions / pit, labour charges complete as per specifications | 20 | Nos. | 1458 | #NAME? | 29160
1.12 | Cutting of trees girth from 600mm to 900mm including cutting of trunks, branches and removal of stumps, roots stacking of serviceable materials with all lifts and upto a lead of 1000m and earth filling in the depressions/pit, complete as per specifications | 20 | Nos. | 2186 | #NAME? | 43720
1.13 | Providing and Fixing 3m long 25mm dia TMT dowel bars 1.5m inserted in 50mm dia holes below LWL in open foundation upto 3m. drilled in hard rock and grouting in CM 1:1 including necessary bending, hooking, cutting and handling charges complete, including the cost of steel. | 2316 | Nos. | 1615 | #NAME? | 3740340
1.14 | Providing and laying Plum Concrete with cement CC 1:2:4 and 40 : 60 Concrete & Plums concrete having maximum 70% boulders for filling/levelling and site grading as mentioned in the drawing with necessary compaction, vibration, formwork, scaffolding & curing etc. at levels complete., and boulder of uniform average size 200mm. The percentage of aggregate size for PCC shall be revised based on trail mix approved by Engineer incharge. | 39347 | Cum | 5363 | #NAME? | 211017961
1.15 | Providing and constucting pithcing / Revetment of 30 cm thick on slopes using granite/basalt/trap/stones of surface area not less than 0.04 sqm and wedged with spalls including cost of all materials, labour etc., complete as per specification. | 2000 | sqm | 1133 | #NAME? | 2266000
1.16 | Providing and constructing granite/trap/basalt size stone masonry for toe wall with cement mortar 1:4, edges of stones chistle dressed in courses not less than 15cms high, bond stones at two m, apart in each course including cost of materials, labour, scaffolding, curing complete as per specifications. | 300 | Cum | 4873 | #NAME? | 1461900
1.17 | Providing ruled pointing to coursed stone masonry with cement mortar 1:3, 20mm deep, after raking joints to depth of 20mm nicely lining, including cost of materials, labour, curing complete as per specifications. | 300 | sqm | 161 | #NAME? | 48300
| TOTAL CARRIED TO BILL IB SUMMARY |  |  |  |  | 269376435
PART 2B : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - IIB : CONCRETE AND ALLIED WORKS
2.1 | Providing and laying in position plain cement concrete of mix 1:3:6 with OPC cement content at 220Kgs using 40 mm and down size graded granite metal course aggregates @0.84cum and the fine agregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications.
a) | Chlorine building, valve chambers,PCC filling for level difference,etc. | 114 | Cum | 6755 | #NAME? | 770070
2.2 | Providing and laying in position plain cement concrete of design mix M15 1:2:4 with OPC minimum cement content at 240Kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, shuttering, labour, HOM of machinery, curing complete as per specifications. | 1811 | Cum | 6940 | #NAME? | 12568340
2.3 | Providing and laying in position reinforced cement concrete of design mix M25(Minimum cement content of 360kg/m3) as per specifications using 20 mm and down size graded granite metal course aggregates and the fine agregates with superplastisiser conforming to IS9103-1999 reaffirmed-2008, machine mixed, concrete laid in layers not exceeding 15 cms, thick, well compacted, in foundation and plinth , ground floor level for roof slabs, staircase, lintels, etc, including cost of all materials, labour, HOM of machinery, curing complete as per specifications for chlorine house and security cabin,etc. | 3971 | Cum | 7912 | #NAME? | 31418552
2.4 | Providing and laying cement concrete in position reinforced cement concrete of design mix M30(Minimum cement content of 400kg/m3) as per specifications by pumping using 20 mm and down size granite Coarse aggregates & fine aggregates of ready mixed concrete (RMC) for R.C.C works laid in 15 cms thick layers and well compacted including vibrating, curing, including smooth finish in CM 1:3, with all lead and lifts etc., complete (exclusive of cost of steel and fabrication charges.) Ready Mixed Concrete for raft foundation, walls, Beams, Columns, underground chambers, baffle walls, Staircase,roof,etc., complete as per specifications. | 6448 | Cum | 8530 | #NAME? | 55001440
2.5 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons.(Type F1 finish)
a) | Reservoir,Chlorine House ,security cabin,etc., | 1224 | sqm | 729 | #NAME? | 892296
2.6 | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 8667 | sqm | 729 | #NAME? | 6318243
b) | Level from 3.50 to 4.50m | 2419 | sqm | 729 | #NAME? | 1763451
c) | Level from 4.50 to 5.50m | 2419 | sqm | 729 | #NAME? | 1763451
d) | Level from 5.50 to 6.50m | 2177 | sqm | 729 | #NAME? | 1587033
2.7 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 1254 | sqm | 729 | #NAME? | 914166
b) | Level from 3.50 to 4.50m | 346 | sqm | 729 | #NAME? | 252234
c) | Level from 4.50 to 5.50m | 322 | sqm | 729 | #NAME? | 234738
d) | Level from 5.50 to 6.50m | 300 | sqm | 729 | #NAME? | 218700
e) | Level from 6.50 to 7.50m | 100 | sqm | 729 | #NAME? | 72900
2.8 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Beams Level from 0.00 to 3.50m | 1594 | sqm | 729 | #NAME? | 1162026
b) | Beams Level upto 4.50m | 339 | sqm | 729 | #NAME? | 247131
c) | Beams Level upto 10m | 381 | sqm | 729 | #NAME? | 277749
2.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs, landing, balconies and likes thickness upto 200 mm including cost of all materials, labours, complete as per specifications. (Type F2 finish)
a) | Reservoir, Chlorine house,security cabin,etc., | 5556 | sqm | 729 | #NAME? | 4050324
2.1 | Providing TMT bars of Fe 500(CRS) grade steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 854 | MT | 71308 | #NAME? | 60897032
2.11 | Providing TMT bars of Fe500 grade steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 27 | MT | 67665 | #NAME? | 1826955
2.12 | Fabricating and supplying anchor bolts, pipe sleeves, channels, angles, plates and all other types of inserts in concrete members and placing them in position as specified on drawings at all locations and at all levels including two coats of approved oil paint over one coat of zinc-rich primer over exposed surfaces. | 850 | kg | 108 | #NAME? | 91800
2.13 | Filling of box-outs left in RCC walls, etc after erection of pipes, inserts in reinforced concrete of grade M30 with coarse aggregate of size 20 mm downgraded, including roughening and preparing internal surfaces of box-outs, adding expansive agents to concrete, shuttering for Class F2 finish, compacting, curing, finishing etc complete but excluding reinforcement wherever specified.
a) | For M30 grade concrete (Minimum cement content of 400kg/m3) | 165 | Cum | 9511 | #NAME? | 1569315
| TOTAL CARRIED TO BILL IIB SUMMARY |  |  |  |  | 183897946
PART 2B : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - IIIB : GENERAL BUILDING WORKS
3.1 | Providing and laying 230 mm thick rubble packing in plinth with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, including spreading 12 mm layer of stone grit on top, etc., complete for all building works as per drawings, details and specifications. | 435 | sqm | 713 | #NAME? | 310155
3.2 | Providing and constructing precast concrete solid blocks with compressive strength not less than 35kg. per sqm with cement mortar 1:4 masonry (quoin, Jamb, closer blocks) with solid concrete blocks of size 40X20X20 cms conforming to IS.2185/ 1965 in superstructure including cost of materials, labour charges, double scaffolding, curing complete as per specifications. | 176 | sqm | 1454 | #NAME? | 255904
3.3 | Providing plastering to masonry including providing and removing double scaffolding rounding of all corners whever required smooth rendering curing etc., complete as per specifications with burnt brick masonry plain plastering 20mm thick in CM 1:4 (external) | 898 | sqm | 336 | #NAME? | 301728
3.4 | Providing plastering to masonry including providing and removing scaffolding rounding of all corners whever required, smooth rendering curing etc complete as per specifications with burnt brick masonry plain plastering 12mm thick in CM 1:4 with lime rendering (internal) | 1208 | sqm | 283 | #NAME? | 341864
3.5 | Providing and finishing external walls in two coats with waterproof cement paint and primer of approved brand and shade to give an even shade after throughly brooming the surface to remove all dirt and loose powdered material, free from mortar drops and other foreign matter cost of materials, labour, complete as per specifications.
a) | Reservoir,Chlorine House and watchman cabin,etc. | 4337 | sqm | 175 | #NAME? | 758975
3.6 | Providing and applying painting in two coats with plastic emulsion paint and primer of approved brand on wall surface to give an even approved shade after thoroughly brushing the surface, free from mortor drops and other foreign matter including preparing the surface even and sand paper smooth, cost of materials, labour, complete as per specifications.
a) | Chlorine House and security cabin,etc. | 2029 | sqm | 178 | #NAME? | 361162
3.7 | Providing and laying flooring and steps fine machined polished granite stone slabs of approved colour 20mm thick on cement mortar bed 1:6, 20mm thick, and, joints finished with cement mortar 1:3 over existing cement concrete bed ,including cost of materials, labour, curing complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin.etc. | 37 | sqm | 4372 | #NAME? | 161764
3.8 | Providing and fixing skirting of 300mm high using prepolished water cut/gang saw of 19mm thick grey granite 0.5mm wide chamfered width and depth and fixing in CM 1:4 of 20mm thick after chipping the walls, etc., including cost of all materials, mortar,labour,curing,etc., complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin,etc | 100 | RM | 1312 | #NAME? | 131200
3.9 | Providing dado, rises of steps with colour glazed tiles on 10mm thick cement plaster 1:3 and jointed with white cement slurry over rough plaster surface ( excluding cost of rough plastered surface which should be measured and paid separately) using glazed tiles of approved make and size including cost of materials, labour, complete as per specifications.
a) | chlorine house, reservoir staircase,etc | 19 | sqm | 1299 | #NAME? | 24681
3.1 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tiles of approved make and colour of size 100 mm x 200 mm x 20 mm thick for flooring, on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Neutralization pit, walls and base slab | 145 | sqm | 4070 | #NAME? | 590150
3.11 | Providing and laying M-15 cement concrete flooring, 60mm thick with metallic concrete hardner topping, under layer of 45mm thick M-15 cement concrete using broken granite metal of 20mm and downsize and top layer of 15mm thick metallic cement hardner consisting of mix 1:2 by volume, with metallic hardening compound of approved quality mix in the ratio of 4:1, including finishing, cost of materials, labour, curing, complete as per specifications.
a) | Drum room and chlorinator room | 75 | sqm | 886 | #NAME? | 66450
3.12 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tile dado of approved make and colour of size 100 mm x 200 mm x 20 mm thick for on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Drum room and chlorinator room | 190 | sqm | 4070 | #NAME? | 773300
3.13 | Providing and fixing ceramic tiles (non skid) of size 400x400mm for flooring laid on a bed of 20mm thick cement mortar 1:3 mix flush pointing with white cement mixed with matching colour pigment including curing, cleaning,etc., complete.The work includes cost of all materials,mortar,labour charges for all items of work,hire charges for equipment,etc., complete as per specifications.
a) | Wash room of control and Office rooms | 10 | sqm | 1325 | #NAME? | 13250
3.14 | Providing, fabricating and fixing in position anodised aluminum doors using following aluminum sections mat or glossy finish, outer frame of section 101.6 x 44.45 x 3.18 mm at 2.404 Kg/m, door shutters vertical section - 44.62 x 44.45 x 3.00mm at 1.426 Kg/m, bottom section 114.3 x 44.45 x 3.18mm at 2.646 kg/m, top section 47.62 x 44.45 x 3.00mm at 1.426 kg/m, middle section 49.91 x 44.45 x 3.00mm at 1.495 Kg/m, glazing clips 19 x 17.3x 11mm x 0.90 mm thick at 0.124 kg/m, all sections anodised to 12 to 15 microns. Cut to length, joint mitred corners grinded, shutters pivoted opening arrangement with h eavy duty aluminum alloy automatic door closer, floor mounted, providing and fixing standard approved accessories such as aluminum handle, for full width or length, tower bolts, lock pivots, PVC or rubber gaskets with 5.5 mm thick plain glass for top and bottom panel, aluminum sections treated for removal of rust, coated with greasy material for non adherence of mortar or any sticky material, the assembled frame fitted with corner angles, strips and fitted with rawl plugs, or teak wood gutties, to RCC columns, or masonry sides, including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. as per specifications | 24 | sqm | 9472 | #NAME? | 227328
3.15 | Providing, fabricating and fixing in position Stainless steel doors including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. | 3 | sqm | 36429 | #NAME? | 109287
3.16 | Providing and fixing mechanical gear type rolling shutters of approved make out of 18 guage, 75mm wide cold rolled steel laths of convex corrugation, with side guides and bottom rail, with interlocking arrangements for steel laths by means of alternate clips, suspension shaft with High tension coil type springs two numbers, mounted on specially designed pipe shaft, with bracket plates, guide channels, ball bearing arrangements, for inside & outside locking complete including pulling hooks, 4Nos. handles with all fittings and accessories, painted with a coat of red lead paint (without top cover) cost of materials, labour, HOM of machinery complete as per specifications. | 12 | sqm | 7286 | #NAME? | 87432
3.17 | Providing and fixing hydraulic door closures -Aluminium body | 5 | Nos. | 2915 | #NAME? | 14575
3.18 | Providing and fixing mortice door lock heavy duty to doors. | 9 | Nos. | 2186 | #NAME? | 19674
3.19 | Providing and fixing in position anodized aluminium windows and ventilators as per approved drawings with sliding shutters using double track window frame section of size 61.85x31.75mm. with 1.2mm thick, bottom section weight 0.695 kg/m, sides and top sections 1.3 mm. thick weight 0.659 kg/m; and shutter comprising top and bottom section of size 40mmx18mm, 1.25mm thick 0.417 kg./m; shutter outer side 40mmx18mm, 1.25mm.thick weight 0.417 kg/m, shutter interlock section 40mmx26.7mm, 1.1mm thick, weight 0.469 kg/m. the shutters mounted on nylon rollers with approved quality of fixtures such as aluminium handles tower bolts etc.; and providing and fixing 5.5mm. thick plain glass for shutters fitted with rubber beading aluminium sections anodised 12 to 15 microns, including cutting to required length, joints mitred subdividing the frame tenonned and rivetted in the assembled frame stiffened with end clips at corners angles etc., and fixed to the walls, lintels, floor beams/cills as the case may be with necessary steel screws, raul plugs, or teak wood gatties including cutting masonry or concrete and making good the original surface using cement mortar, aluminium sections pretreated for removal of any rust and protection of further rust formation and coated with the greasy materials for non- adhesion of mortar and any other sticky materials, (this coating should be cleaned after installation) including cost of all materials, fixtures, labour and HOM of machinery complete as per specifications. | 65 | sqm | 7286 | #NAME? | 473590
3.2 | Providing, fabricating, assembling and fixing in position aluminium partitions with aluminium section anodized to 12-15 microns using sections in combination of plain, single grove and double grove as per requirements for the frames of overall size 101.6mm x 44.45mm, 3.18mm.thick having section weight, plain sections 2.40kg/m single grove section 2.541kg/m. and double grovesection 2.683 kg/m and bottom 46 kg/m; aluminium louvres of size 77.6mmx27.6mm 1.7mm. thick section weight 0.483kg/m; bottom portions provided with 12mm. thick prelaminated sheet both side of approved colour lamination exterior grade; aluminium sections of mat finish or glossy finish using section, spacing of vertical member shall not exceed 0.6 m. c to c; sections are cut to the required lengths, joints mitered and corners grinded subdividing frames tennoned and rivetted to the frames, the assembled frame should be stiffened with corner angles stripped and fixed with screws, rawl plugs and teak wood gutties to R.C.C.columns or masonry on sides, R.C.C. lintels or beams at top and floor at bottom, including cutting chistling and making good with cement mortar to match the surface, providing and fixing bottom panel filled with the materials to a height of 0.9m. from floor level; and 5.5mm. thick plain glass for middle portion viz., 0.9m. to 2.13 m. and top panel with lower sections, the glass and panels fitted with glazing clips of 19mmx17.3mm. with thickness of 0.9mm. weight 0.124kg/m; aluminium sections pre-treated for removal of any rust and prevention of further rust formation, and coated with greasy materials for non-adherence of mortars or any other sticky materials; vertical members embedded in the flooring by making suitable size holes and fixing with cement mortar, with necessary opening for fixing of doors of standard size including cost of materials, fixtures, labour and HOM of machinery complete. | 17 | sqm | 9472 | #NAME? | 161024
3.21 | Providing and fixing 225 mm wide and minimum 6 mm thick continuous PVC waterstops of approved quality at contraction and expansion joints as per manufacturer's instructions at all levels for Ground level reservoir. | 4695 | RM | 365 | #NAME? | 1713675
3.22 | Supplying and fixing PVC encapsulated CI rungs to shapes and at locations specified in drawings and specifications for Valve chambers | 35 | kg | 108 | #NAME? | 3780
3.23 | Providing and fixing 10 gauge aluminium sheet to required shape and size with rawl plugs and screws to concrete curbs to cover up expansion joints at roof level, including filling the notch with bitumen as specified in drawing, for Ground level reservoir. | 50 | sqm | 2264 | #NAME? | 113200
3.24 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant Type A) in a groove of size 15 mm x 20 mm deep at contraction joints including forming groove as specified on drawing for Ground level reservoir. | 4065 | RM | 387 | #NAME? | 1573155
3.25 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant type B) in a groove of size 25 mm x 20 mm deep at expansion joints including forming groove as specified on drawing for Ground level reservoir. | 2100 | RM | 401 | #NAME? | 842100
3.26 | Providing and fixing in position 25 mm thick sellotex board/filler compound as per standards and approved by the Engineer, of required sizes at expansion joints as specified in drawing for Ground level reservoir. | 265 | sqm | 328 | #NAME? | 86920
3.27 | Providing and laying 500 gauge polyethylene sheet of approved make and quality on blinding layer and wherever specified as directed by Engineer, for Ground level reservoir. | 3785 | sqm | 62 | #NAME? | 234670
3.28 | Providing and fixing slip-strip (1 mm thick PVC sheet) of approved quality or equivalent at junction between top of wall and bottom of roof slab in two layers as directed by Engineer, for Ground level reservoir. | 125 | sqm | 729 | #NAME? | 91125
3.29 | Providing and laying in position yelahanka tiles of size 125 x 250mm of approved quality and make, over a bed of cement mortar 1:3 with thickness varying from 100mm to 25mm including weather proof course and pointed with cement mortar 1:3 mix with red oxide including curing cost of materials, labour complete as per specifications. | 372 | sqm | 1403 | #NAME? | 521916
3.3 | Providing and fixing 150 mm diameter cast iron air ventilators as per design & shape indicated in drawings over roof slab of all reservoirs with mosquito proof jali etc complete. | 75 | Nos. | 6896 | #NAME? | 517200
3.31 | Installing precast circular hume pipe septic tank suitable for 5 persons capacity conforming to IS 2470, and constructing standard soak pit for the same capacity, including excavation and backfilling of pit, PVC Pipe, filling soakpit with broken bricks, overflow connection precast RC slab and construction of manhole chamber with cover, C.I. vent pipe with cowl and connecting it to incoming and outgoing pipelines etc., complete. | 1 | Nos. | 145713 | #NAME? | 145713
3.32 | Supplying of and application of food grade epoxy painting on the inside surface of GLR headroom, GLR inside staircase and wall face at staircase complete, as per applicable Technical specification clause, including all labour, HOM of equipment, lead, lifts taxes etc., complete, including all surface preparation, testing, Rate shall be inclusive of all materials, tools and plants, testing and inspection etc., complete. | 1950 | sqm | 481 | #NAME? | 937950
3.33 | Providing and laying M15 grade plain concrete in screed for required level above base slab of reservoir to specified slope with coarse aggregate of size 10mm downgraded including formwork and compacting with a hand rammer,curing,finishing,etc., complete as per specifications. | 800 | Cum | 6871 | #NAME? | 5496800
3.34 | Providing and laying plain cement concrete of design mix M15 with OPC minimum cement content at 240kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers with thickness varying from 150mm to 75mm over 230 mm thick rubble packing with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, etc., complete for plinth protection 1m wide as per drawings, details and specifications. | 100 | RM | 1689 | #NAME? | 168900
| TOTAL CARRIED TO BILL IIIB SUMMARY |  |  |  |  | 17630597
PART 2B : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - IVB : WATER SUPPLY AND SANITARY WORKS
4.1 | Providing and fixing white vitreous china clay, water closet European type (Pedestal type, P-trap) with black solid plastic seat and lid, CP brass hinges, rubber buffers, 10 litre low level, P.V.C flushing cistern (all are approved make) with fittings, SS brackets, 40mm diameter flush bend with fittings and clamps, overflow arrangements with specials and 25mm mosquito proof coupling of approved design, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 14572 | #NAME? | 29144
4.2 | Providing and fixing white vitreous china clay, flat back wash basins of size 550 mm x 400 mm with a pair of 15mm C.P brass pillar taps with SS brackets, 32mm C.P brass waste of standard pattern, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 8743 | #NAME? | 17486
4.3 | Providing and fixing white vitreous china clay, flat back, lipped front urinal basin of 430x260x350mm in the range of three with 7.5 litres PVC automatic flushing cistern, SS brackets, standard flush pipe and C.P brass spreaders with brass unions and G.I clamps painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 7286 | #NAME? | 14572
4.4 | Providing and fixing in position brass bib cock of aproved quality 15mm nominal bore including cost of all materials, labour and HOM of equipments with all leads complete as per specifications. | 3 | Nos. | 1458 | #NAME? | 4374
4.5 | Providing brick masonry inspection chambers, rectangular in size 90 cm x 45 cm and upto 1.5 m depth on sewer line , with 230 mm brick wall in cement mortar (1:2), plastered both inside and outside with 20 mm thick cement mortar (1:2),including 1.6 m x 1.2 m x 290 mm thick cement concrete 1:2:4 in haunches as per standard plan including excavation, backfilling the excavated sides and removing surplus earth and with heavy duty C.I. cover and frame and with M.S. steps fixed in cement mortar with cement and sand filleting. | 2 | Nos. | 26223 | #NAME? | 52446
4.6 | Same as in for item 4.5 above but for depth greater than 1.5 m and upto 3 m | 2 | Nos. | 38907 | #NAME? | 77814
4.7 | Constructing circular type manhole 1500mm internal dia at bottom, 525mm dia at top, in wire cut burnt brick masonry with 1:5 cement mortar, cement plaster 1:3, finish with a floating coat of neat cement, RCC 1:2:4 top slab using 20mm and downsize granite metal, foundation concrete, M7.5 using 40mm and downsize granite metal and making channels in cement concrete M15 using 20mm and downsize granite metal, neatly finished curing, fixing CI cover complete including external, footrests and 12mm thick cement plaster on the external surface, cost of materials, labour charges, HOM of machineries complete as per specifications. | 2 | Nos. | 75964 | #NAME? | 151928
4.8 | Providing and fixing PVC Nahani trap of approved make conforming to ISI specifications and construction of cistern in M-15 as per directions. (rate inclusive of cost of materials and fixtures and conveyance of materials to work spot). | 3 | Nos. | 875 | #NAME? | 2625
4.9 | Providing stoneware gully trap of approved quality and make fixing in M-15 and plastering with CM 1:3 wherever necessary. (rate includes cost of all materials, fixtures and lead). With 100mm outlet. | 2 | Nos. | 1458 | #NAME? | 2916
4.1 | Providing and fixing 75 mm dia PVC slotted vent cowls conforming to IS 3989 with necessary fixtures and as directed by Engineer. | 2 | Nos. | 729 | #NAME? | 1458
4.11 | Providing and fixing white glazed 'P' trap as per IS 2556 (Part 7) 100 mm dia with SS grating 10 mm thick etc., complete. | 1 | Nos. | 1458 | #NAME? | 1458
4.12 | Providing and fixing cast copper alloy stop valves, polished bright, conforming to and as per IS 781.
a) | 25 mm dia. | 1 | Nos. | 729 | #NAME? | 729
b) | 20 mm dia. | 2 | Nos. | 729 | #NAME? | 1458
c) | 15 mm dia. | 1 | Nos. | 729 | #NAME? | 729
4.13 | Providing and fixing SS towel rail 740mm length, 20mm dia with C.P brackets, fixed to wooden cleats with C.P brass screws including cost of materials, labour complete as per specifications. | 4 | Nos. | 2186 | #NAME? | 8744
4.14 | Providing and fixing best quality SS liquid soap bottle holders of approved make with SS brackets, screws, rawl plugs, etc. complete. | 3 | Nos. | 1458 | #NAME? | 4374
4.15 | Providing and fixing 600x450 bevellead edge mirror of superior glass with 6mm hard board backing and fixed to wooden cleats with C.P screws, washers, including cost of materials, labour complete as per specifications. | 4 | Nos. | 7286 | #NAME? | 29144
4.16 | Providing and fixing white glazed partition walls of size 825 mm x 450 mm x 25 mm as per IS 2556 (Part 6 ) of approved make, properly supported with C.I. brackets, etc. complete. | 2 | Nos. | 2911 | #NAME? | 5822
4.17 | Providing and fixing UPVC water pipes and fittings 'B' class pressure rating of 10kg/cm2 conforming to IS 13592 and IS14735, with all necessary fixtures and bends, including testing the line as specified,etc.,complete.
a) | 25 mm dia. | 100 | RM | 292 | #NAME? | 29200
b) | 20 mm dia. | 25 | RM | 219 | #NAME? | 5475
c) | 15 mm dia. | 10 | RM | 146 | #NAME? | 1460
4.18 | Providing and Fixing PVC soil waste and vent pipes 100 mm diameter - 10kg/cm2 with spun yarn soaked in cement slurry and cement mortar 1:2 including cost of materials, labour, testing complete as per specifications. | 200 | RM | 875 | #NAME? | 175000
4.19 | Providing and fixing PVC pipes of approved make and 150 mm dia - 10kg/cm2 conforming to IS 651, including all necessary fixtures and bends, including excavation, backfilling, testing etc., complete as per specification. | 200 | RM | 1284 | #NAME? | 256800
4.2 | Providing and fixing 100 mm dia - 10kg/cm2 PVC rain water pipes as per IS: 4984 including all fixtures such as brackets, bends etc.as directed by the Engineer. | 765 | RM | 315 | #NAME? | 240975
4.21 | Providing and fixing cast iron bell mouth rain water outlets including MS grating, etc., complete as directed by Engineer.
a) | 100mm Dia. | 90 | Nos. | 1458 | #NAME? | 131220
4.22 | Providing, supplying and fixing rectangular SS manhole covers with chains connecting to the frame of size 1200x900 and 900mm x 600mm of grade 304L for roof slab of reservoir and underground chambers at locations shown in drawing including SS frame etc. complete. | 750 | kg | 583 | #NAME? | 437250
4.23 | Supplying PVC pipes conforming to IS 4985:2000 with latest amendments and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations and cuts of pipes wherever necessary including jointing of PVC and specials with jointing of approved type, with all labour with all lead & lifting. (75mm dia - 10kg/cm2) | 65 | RM | 729 | #NAME? | 47385
| TOTAL CARRIED TO BILL IVB SUMMARY |  |  |  |  | 1731986
PART 2B : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - VB : STRUCTURAL STEELWORKS
5.1 | Supplying, fabricating, delivering to site, loading, unloading, etc. and erecting structural steel work for the following works, including one shop coat of red oxide zinc chromate primer after fabrication and one coat of the same after erection and two coats of synthetic enamel paint of approved shade, etc. complete as per specifications.
a) | Chlorine house | 7157 | kg | 108 | #NAME? | 772956
5.2 | Providing and fixing in position MS ladders as per drawing, including painting etc. complete. | 191 | kg | 117 | #NAME? | 22347
5.3 | Providing and fixing 304- grade Stainless steel handrails of 14 gauge pipe for ramps or staircase are made out of stainless steel hollow pipes, using 50mm dia for verticals @ 1.60mtr c/c are fixed to the rams or steps by drilling with bolts and 100mm dia MS base plates 10mm gauge for fixing of vertical pipes 4 nos anchor bolts & 40mm dia pipes are fixed horizontally for 2 rows top one pipe are fixed with vertical pipes another one are fixed with elbows & 25mm dia pipes are fixed horizontally for 2 rows with elbow top measure @ equal intervals including cutting, welding, bending wherever necessary with suitable caps @ tops, bottoms, corners finishing with mat/shining etc., completeincluding cost and conveyance of all materials, labour for all items of work, HOM of euipment with all lead and lift, loading and unloading, transportation charges and all other incidental charges etc., complete as per specification and directions of the Engineer-in-charge of the work. Ramps or staircase for physically challenged. | 345 | RM | 2889 | #NAME? | 996705
5.4 | Providing and fixing MS frame with 10 mm thick flats with grating cover with stiffeners for openings as specified in drawing at all locations and levels, including painting, etc., complete. | 1935 | kg | 108 | #NAME? | 208980
| TOTAL CARRIED TO BILL VB SUMMARY |  |  |  |  | 2000988
PART 2B : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - VIB : ROADWORKS
ROADS & DRAINS
6.1 | Construction of Granular sub-base for 200 mm by providing coarse graded material , spreading in uniform layers on prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density, complete as per clause 401 for Grading-v of MORTH V Specifications. | 480 | Cum | 2851 | #NAME? | 1368480
6.2 | Providing, laying, spreading and compacting 150 mm graded stone aggregate to Wet Mix Macadam (WMM) specification including premixing the material with water at OMC in mechanical mix plant carriage of mixed material by tipper to site, laying in uniform layers in sub base/ base course on well prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density. MORTH clause 406 | 240 | Cum | 3078 | #NAME? | 738720
6.3 | Providing and applying Primer Coat with bitumen emulsion using emulsion pressure distributor at the rate of 0.60 kg per sqm on the prepared WMM surface including cleaning of WMM surface and spraying primer using mechanical spray jet as per MORTH V specification clause No. 502 complete in all respects. | 2400 | sqm | 34 | #NAME? | 81600
6.4 | Providing and applying Tack Coat on the prepared WMM surface hot bitumen primed at 1Kg per Sqm heating bitumen in boiler fitted with spray set as per MORTH V specification clause No. 503 complete in all respect. | 2400 | sqm | 57 | #NAME? | 136800
6.5 | Providing and laying Bituminous Macadam 50 mm thick from 100-120TPH hot mix plant using crushed aggregates of specified grading premixed with bituminous binder, transported to site, laid over a previously prepared surface to the required grade, level and alignment and rolled by virbratory roller as per MORTH V specification clauses 505 to achieve the desired compaction complete with all lead and lift and direction of Engineer-in-charge. | 100 | Cum | 10448 | #NAME? | 1044800
6.6 | Providing and applying Tack Coat on the prepared BM surface at 0.5Kg / Sqm heating bitumen in boiler fitted with spray set as per specification clause No. 503 of MORTH V complete in all respects. | 2000 | sqm | 28 | #NAME? | 56000
6.7 | Providing and laying Semi Dense Bituminous Concrete(SDBM) 25 mm thick with 100-120 TPH hot mix plant using crushed aggregates of specified grading, premixed with bituminous binder 5.4 to 5.6 per cent of mix and filler, transporting the hot mix to work site, laying with a hydrostatic paver finisher with mechanical control to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause No. 508 complete with all lead and lift, with 60/70 Grade bitumen and direction of Engineer-in-charge. | 50 | Cum | 11361 | #NAME? | 568050
6.8 | Construction of coverd drain 0.3m x 0.45m (inside dimensions) with RCC M20 grade 10cm thick for walls and floor, laid over 10cm thick 1:3:6 PCC bed and covered with M30 grade RCC slab 0f 15cm thick excluding earth work including reinforcement @ 35 kg/rmt and form work complete as per specifications. | 1000 | RM | 5724 | #NAME? | 5724000
COMPOUND WALL
6.9 | Earthwork excavation for foundation in all types of soil excluding hard rock including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50 m and disposal of excess excavated earth including all leads and lifts after breaking of clods complete as per specifications.
a) | 0 -1.5m | 1751 | Cum | 152 | #NAME? | 266152
6.10 | Providing and laying in position plain cement concrete of mix M10 with OPC cement @220kgs, with 20mm and down size graded granite metal coarse aggregates @ 0.84cum and fine aggregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms thick, well compacted, in foundation and plinth including cost of all materials, labour, HOM of machinery curing complete as per specifications. | 47 | Cum | 6409 | #NAME? | 301223
6.11 | Filling available excavated earth (excluding rock) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts including cost of labour complete as per specifications. | 94 | Cum | 73 | #NAME? | 6862
6.12 | Providing and laying in position Reinforced Cement Concrete of Grade M25 (Design mix) with 20mm and downsize graded granite metal machine mixed, concrete laid in layers not exceeding 15 cm thick, vibrated for R.C.C. beams, columns of all sizes in foundation, plinth and superstructure ground floor levels of roof slabs, base slab, staircases, lintels, columns including cost of all materials, labour, HOM of machinary, curing, complete as per specifications. | 165 | Cum | 7617 | #NAME? | 1256805
6.13 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for foundation, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specifications | 768 | sqm | 729 | #NAME? | 559872
6.14 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per speciications. | 816 | sqm | 729 | #NAME? | 594864
6.15 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications | 112 | sqm | 729 | #NAME? | 81648
6.16 | Providing TMT Steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, tying with binding wire and anchoring to the adjoining members whenever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinary complete as per specifications. (Fe 500 grade confirm to IS 1786). | 22 | MT | 69122 | #NAME? | 1520684
6.17 | Providing barbed fixed 12x12 guage drawn into stone pillar or iron pillars including drawing in holes wherever necessary excluding the cost of pillar but including the cost of barbed wire and binding wire etc., complete | 2000 | RM | 132 | #NAME? | 264000
6.18 | M.S Angle | 280 | kg | 108 | #NAME? | 30240
6.19 | Providing and finishing external walls in two coats with waterproof paint with primer of approved brand and shade to give an even shade after thoroughly brooming the surface to remove all dirt and loose powdered material free from mortar drops and other foreign matter cost of materials, labour complete as per specifications | 2000 | sqm | 175 | #NAME? | 350000
6.20 | Supplying and fixing M.S rectangular poles made out of 2 equal angles of 65x65x6 mm welded together and fixed in CC (1:2:4) with 2 nos 16mm dia MS hold fast rods each of length 25cms including cost of all materials cutting,bending,scaffolding wherever necessary,nicely finishing the welded joints with all lead lifts and as per specifications including providing 2 coats of approved quality paint over one coat of shop painting. | 800 | RM | 1337 | #NAME? | 1069600
6.21 | Providing chain link fencing 50mm size of 8 guage properly stretched between rectangular poles and fixed with suitable bolts & nuts, the free ends shall be welded to the pole and block pipe at top and bottom as required including cost of all materials, labour, lead and lifts and as per the directions of the Engineer in-charge of work including two coats of approved quality paint over one coat of shop paint. | 1000 | sqm | 365 | #NAME? | 365000
6.22 | Providing and fixing MS block pipe of 38mm dia of heavy guage of 14 including removing the bends, cutting the pipe, and fixing pipe in between the two vertical poles (MS rectangular poles) and spot welding the chain linkwith MS block pipe including cost of all materials wastage in cutting, scaffolding wherever necessary with all lead and lift,etc., complete including two coats of approved quality paint over one coat of shop paint. | 640 | RM | 209 | #NAME? | 133760
6.23 | Providing and erecting in position., 2400x600x60 mm thk precast slab panels of M25 grade reinforced cement concrete including reinforcement and formwork with coarse aggregate of size 20mm downgraded with minimum cement content of 320kg/cum. The reinforcement consists of 1 no of 10mm dia loop and round the panel, 5 nos of 8mm dia horizontals and 15 nos of 8mm dia verticals equally spaced. The thickness of the panel shall be 60mm thick at the middle and 70mm thick at the edges for a width of 250mm.The gaps between the panels shall be packed with 1:4 cement mortar and the final surface between the panel and RCC post shall be finished using silicon sealant of approved make, complete as per specification & drawing.
a) | For both side plain finished panels of 2400mm x 600mm size, as shown in the drawings. | 160 | Nos. | 3524 | #NAME? | 563840
b) | For one side plain and other side with horizontal grooves as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 160 | Nos. | 3524 | #NAME? | 563840
c) | For one side plain and other side with vertical grooves as as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 160 | Nos. | 3524 | #NAME? | 563840
d) | For one side plain and other side with BWSSB logo as per the pattern panels of 2400mm x 600mm size, as shown in the drawings. | 160 | Nos. | 3524 | #NAME? | 563840
6.24 | Providing and fixing gates consisting of 40 mm NB light glass GI pipes external framework and 8 x 30 MS flats internal framework with 16 guage MS jointing plates and tack welded over the framework with necessary hinges and locking arrangement, including painting over approved primer coat, etc. all complete as per specifications and drawings. | 2 | MT | 107603 | #NAME? | 215206
| TOTAL CARRIED TO BILL VIB SUMMARY |  |  |  |  | 18989726
PART 2B : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - VIIB : PIPEWORKS, VALVES AND SPECIALS
Pipelines, Specials and Appurtenances
7.1 | Providing, Fabricating, shop welding, transporting, handling, aligning, laying and jointing / welding of MS pipes of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate also include loading and unloading, radiography of joints as specified and hydraulic testing of pipeline to specified pressure as per specifications and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings.
a) | 900 mm internal diameter with 6 mm shell thickness Overflow Pipe of GLR | 30 | RM | 10461 | #NAME? | 313830
b) | 800 mm internal diameter with 6 mm shell thickness Outlet Pipe of GLR | 20 | RM | 9306 | #NAME? | 186120
c) | 700 mm internal diameter with 5 mm shell thickness Inlet Piping of GLR | 40 | RM | 6784 | #NAME? | 271360
7.2 | Providing, fabricating, shop welding, handling, transporting, aligning, laying and jointing of MS specials of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate include loading and unloading, radiography of joints as specified and hydraulic testing of specials to specified pressure and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings. | 1250 | kg | 139 | #NAME? | 173750
7.3 | Providing guniting (CM 1:3 over 50 x 50 mm weld mesh of 13 gauge) on the external surface of pipes and specials including supplying and fixing reinforcement as per specifications after cleaning the pipes including curing etc., at fabrication yard and guniting the field joints at site between two pipes after testing complete in all respects as per specifications.
a) | 913 mm OD pipes and specials, 25 mm thick guniting | 87 | Sq.m | 729 | #NAME? | 63423
b) | 813 mm OD pipes and specials, 25 mm thick guniting | 52 | Sq.m | 729 | #NAME? | 37908
c) | 711 mm OD pipes and specials, 25 mm thick guniting | 90 | Sq.m | 729 | #NAME? | 65610
7.4 | Providing food grade internal epoxy lining of 0.5 mm thick as per specifications to the internal surfaces of mild steel pipeline, fittings, specials etc., including surface preparation, machine lining, curing and testing / inspection etc., complete.
a) | 900 mm ID pipes & specials to 900 mm finished diameter, 0.5 mm thick internal epoxy lining | 85 | Sq.m | 583 | #NAME? | 49555
b) | 800 mm ID pipes & specials to 800 mm finished diameter, 0.5 mm thick internal epoxy lining | 50 | Sq.m | 583 | #NAME? | 29150
c) | 700 mm ID pipes & specials to 700 mm finished diameter, 0.5 mm thick internal epoxy lining | 88 | Sq.m | 583 | #NAME? | 51304
7.5 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Manually operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 800 mm dia PN 16 for 800 mm ID | 1 | No. | 847229 | #NAME? | 847229
b) | 700 mm dia PN 16 for 700 mm ID | 1 | No. | 576799 | #NAME? | 576799
7.6 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Motorised operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 700 mm dia PN 16 for 700 mm ID | 2 | No. | 686789 | #NAME? | 1373578
b) | 800 mm dia PN 16 for 800 mm ID | 2 | No. | 808026 | #NAME? | 1616052
7.7 | Supply,installation, testing & Commissioning of (Scour purpose) Ductile Iron (DI) Resilient seated soft sealing sluice valve. Detailed Valve specifications & arrangement shall be as defined in Volume 2. The rate is inclusive of cost of mating flanges, valve,bolts & nuts and rubber insertions,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 300 mm dia. PN 16 size scour valves for GLR | 2 | No. | 55047 | #NAME? | 110094
7.8 | Providing, supplying and fixing SS 304 Expansion Bellows with Flange Ends as per specifications and drawings.Detailed Specifications & arrangement shall be as defined in Volume 2. The rate shall include transportation to site with all leads and lifts, aligning and jointing approved anti-corrosive paint etc., complete in all aspects. Rates are incluisve of Labour Charges.
a) | 800 mm dia. PN 16 | 3 | No. | 134638 | #NAME? | 403914
b) | 700 mm dia. PN 16 | 3 | No. | 125765 | #NAME? | 377295
7.9 | Providing and laying following dia of MS pipes conforming to IS 3589 in trenches outside the pipeline scour valve chambers for draining, include lining & coating, excavation, connecting to scour valve, backfilling the earth etc., complete.
a) | 300 mm dia. 5.6 mm thick | 60 | RM | 3294 | #NAME? | 197640
| TOTAL CARRIED TO BILL VIIB SUMMARY |  |  |  |  | 6744611
PART 2B : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - VIIIB : MECHANICAL WORKS
8.1 | Mechanical Equipment
a) | Supply,Testing, Installation & Commissioing of 4 Kg/hr Capacity with 0-2 ppm dosage level Vaccum type Chlorination System 2 sets.(1W+1S) with all allied works complete as per Bid specification of Volume 2
(i) | 4 Kg/hr | 2 | Sets. | 1621047 | #NAME? | 3242094
b) | Supplying,Testing, Installation & Commissioing of Chlorine gas Filled Chlorine Tonners of 900 Kgs with all allied works complete as per Bid specification of Volume 2 | 2 | Nos. | 189426 | #NAME? | 378852
c) | Supply,Testing, Installation & Commissioing of Electrically operated wire rope hoist of 2 Ton capacity conforming to IS 3938 for chlorine house with suitable I-Beam arrangement and Electrical Panels etc.with all allied works complete as per Bid specification of Volume 2 | 1 | Nos. | 291461 | #NAME? | 291461
d) | Service Water Network system
(i) | Providing, erecting and giving test of Centrifugal Monoblock Pump set conforming to IS 9079 operating at 1500 RPM with pump casing: Cast Iron IS 210 FG Gr.260, Impeller:Bronze IS 318 LTB2, Shaft:SS 410 , Pump Seal: Mechanical Seal, priming funnel, cock, suitable flanges at suction and delivery side. Pump shall have common shaft for pump and motor. Motor shall be suitable for working on 2.0 HP, 415 V + 10%, 3 Ph, 50Hz+/-5% A.C. Supply. Motor shall be TEFC type. Pump set shall be suitable for working at various discharge and head requirements. Pump shall be erected on Provided C.C. foundation block with suitable foundation bolts grouted in C.C foundation block. | 2 | Nos. | 56935 | #NAME? | 113870
(ii) | Pressure Gauge: Supply, delivery at site and fixing of glycerine filled stainless steel pressure gauge of 100 mm Dia. suitable for the above pump sets with nipple, stop cock and three way cock for cleaning and necessary length of SS tubing suitable for mounting on the suction and delivery of pump, including 15 NB isolating valve etc., complete with all lead and lifts etc, complete as per specification | 2 | Nos. | 1909 | #NAME? | 3818
(iii) | Providing and fixing in position brass gate valve with CI wheel (screwed end) 40 mm nominal bore including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 6 | Nos. | 8109 | #NAME? | 48654
(iv) | Providing and fixing in position 40 mm nominal bore non-return valve vertical type of approved make including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 2 | Nos. | 8960 | #NAME? | 17920
(v) | Providing & Fixing to wall,ceiling and floor high density polyethylene pipes 6.00 Kgf/sq.cm working pressure of outside diameter raising mains & exposed distribution pipes with special flange, compression type fittings, wall clips, making good the wall, ceiling and floor, including cost of all materials, labour charges, HOM and testing complete as per specifications.
i | 40 mm dia | 100 | RM | 219 | #NAME? | 21900
(vi) | Providing and placing on terrace,polyethylene water storage tanks with manhole lid and suitable locking arrangements,making holes of suitable diameter for inlet,outlet and overflow pipes,including cost of all materials,labour transportation charges,HOM of equipments and testing complete as per specifications (for 1000 litres capacity) within the GLR Campus. | 1 | Nos. | 14572 | #NAME? | 14572
| TOTAL CARRIED TO BILL VIIIB SUMMARY |  |  |  |  | 4133141
PART 2B : INSTRUMENTATION WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - IXB : INSTRUMENTATION WORKS
9.1 | ICA Items for City reserviors
a) | Designing, Supplying, Installing, commissioning & testing of Ultrasonic level transmitter with following technical parameters at GLR and Interfacing with PLC panel including all required Mounting accessories, factory testing & inspection complete as per specifications. Range : (0 - 10 m) | 2 | Nos. | 62344 | #NAME? | 124688
b) | Supply, delivery at site and fixing of Conductivity type Level Switch (back up to level transmitter), High Level & Low Level sensing - (4point contact) with necessary instrumentation cabling,glands with suitable stub and flange and bolting arrangement for hook-up, as applicable and necessary, factory testing & inspection. Range : (0 - 10 m) | 2 | Nos. | 78049 | #NAME? | 156098
c) | Design, Supply, Installation, Testing of Residual chlorine analyzer at GLR and Interfacing with PLC panel and factory testing for complete functional test & inspection. | 1 | Nos. | 227160 | #NAME? | 227160
9.2 | Instrument & power supply cables, supplies, laying, termination & testing.
a) | Plain annealed multistranded tinned copper conductors; solid polyethylene insulation with each pair screened with aluminium-mylar tape including drain wire, with collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (2 Pair x 1.5 sq.mm) | 140 | RM | 782 | #NAME? | 109480
b) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (12 Core x 1.5 sq.mm) | 180 | RM | 1434 | #NAME? | 258120
c) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (4 Core x 1.5 sq.mm) | 290 | RM | 1141 | #NAME? | 330890
9.3 | Miscellaneous Instruments
a) | Designing.supplying, Installing commissioning & testing of Surge Protection Devices | 6 | Nos. | 32558 | #NAME? | 195348
b) | Designing,supplying, Installing commissioning & testing of online UPS with AC Distribution Board(Min 5 KvA Industrial UPS with 60 min backup on full load of field instrumentation and control equipment inclusive of communication equipment to transfer data to CSC) and factory testing & inspection. | 1 | Nos. | 14650 | #NAME? | 14650
c) | supplying, Installing commissioning & testing of Junction Boxes | 4 | Nos. | 18279 | #NAME? | 73116
d) | supplying, Installing commissioning & testing of Field Instrument enclosures-IP 65 rated for all field instruments. | 7 | Nos. | 8954 | #NAME? | 62678
9.4 | Automation System
a) | Designing.supplying, Installing commissioning & testing of hot standby PLC with 16" colour HMI to control valves and to monitor the level and flow in the facility with required SCADA software.HMI shall be color with touchscreen functionality for complete auto operationm with FAT & SAT as per Contract requirements.(also include integration of flowmeter data (flowmeter’s which has been installed under other contracts) with the PLC based control system for continuous monitoring of both incoming and outgoing flow data at each location. All required cabling for connection, required hardware (splitters) with the PLC based control system shall be integral part of scope of work under this contract) | 1 | No. | 1074393 | #NAME? | 1074393
b) | Designing, supplying, installing, commissioning & testing of CCTV IR water proof camera suitable for upto 100ft.with IR Dome camera, control key board, DVR, Hard Disk, cables, UPT transreceivers etc. complete. (Close Circuit Television System to be installed at the reservoir locations to cover all areas of the facilities) and factory testing & SAT. | 4 | No. | 26866 | #NAME? | 107464
| TOTAL CARRIED TO BILL IXB SUMMARY |  |  |  |  | 2734085
PART 2B : ELECTRICAL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - XB: ELECTRICAL WORKS
LT Electrical Works for GLR Premises
10.1 | Supplying and erecting four pole metal clad ON LOAD change over switch 415V, 125A erected on angle iron /GI frame approved make complete. | 1 | No. | 10257 | #NAME? | 10257
10.2 | Supply, Transportation, loading/unloading, Laying, Installation & Commissioning of Solid Aluminum conductor up to 10 sqmm balance stranded conductor, XLPE Insulated, cores laid up, PVC tape/Extruded Innersheathed for Multicore Cables , Armour (Aluminium wire for single core up to 70 sqmm balance Aluminium strip, Glavanised wire for cables upto 2x10 sqmm, 3x10 sqmm,4x6 sqmm balance all galvanised steel strip), extruded PVC Type ST2 sheathed, 650/1100V grade as per IS 7098(Part 1) 1988, Incoming Cable from nearst 415V overhead line as per ESCOM specifications a) Metering Box to Change Over Switch b) Change Over Switch to 415V Panel Board
a) | 3.5C x 50sq.mm (Al. Conductor) | 70 | Mtr. | 263 | #NAME? | 18410
b) | 3.5C x 50sq.mm (Al. Conductor) - Glands | 4 | No. | 98 | #NAME? | 392
c) | 3.5C x 50sq.mm (Al. Conductor) - Lugs | 16 | No. | 50 | #NAME? | 800
10.3 | 415V PMCC Panel Board (Including Chlorine MCC): Supply, Transportation, Installation, Testing & Commissioning of 415V LT Board of cubicle type with 415V, 50 Hz, 3 PH, TPN, 25 kA for 1 sec, wtih IP-54 enclosure with Bottom entry, consisting of incoming and outgoing feeders with metering and protection with complete accessories as per specification and single line diagram.
a) | Incomer: 125A, 25kA, 4P, MCCB | 1 | No. | 10850 | #NAME? | 10850
b) | Outgoing: 25A TPN MPCB (Motorised Valves) | 4 | No. | 4307 | #NAME? | 17228
c) | Outgoing: 63A TPN MCCB (Indoor Lighting DB 1 & 2, Spare 2Nos.) | 4 | No. | 9074 | #NAME? | 36296
d) | Outgoing: 32A TPN MCCB (2T Crane, Spare 2Nos.) | 3 | No. | 7112 | #NAME? | 21336
e) | Supplying & erecting LED type indicating pilot lamp with LED colours red , yellow and blue, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 1 | Set | 1697 | #NAME? | 1697
f) | Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 32 | No. | 566 | #NAME? | 18112
g) | Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod upto 250A MCCB | 8 | No. | 1465 | #NAME? | 11720
h) | Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 100/5A, 5 VA , class 1 accuracy | 3 | No. | 625 | #NAME? | 1875
i) | Multi Functions Meters - Flush type for M V Panel Board LED type, CT/PT, Voltage, Current, Frequency, Kilowatt, Kilo Volt Ampere, KVAR , KVAH, Run Hours, unbalance(V,A),Rpm, Phase angles,Thd-Class 1 With RS 485 Port | 1 | No. | 10390 | #NAME? | 10390
j) | Supplying, erecting & marking SPMCB 5A in provided distribution board | 3 | No. | 571 | #NAME? | 1713
k) | DOL Feeder a) 25A MPCB - 1No b) Supplying and erecting D.O.L. Starter 400V. 3 phase, 50 cycles with no volt coil and overload element with necessary materials and connected to supply upto 7.5 H.P. - 1No. c)Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. d) Supplying, fixing and wiring 0 to 30amps Ammeter Analog SR 65 5D/5A C.T.operated-AC - 1No. e) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 30/5A, 5 VA , class 1 accuracy - 1No. | 8 | No. | 8943 | #NAME? | 71544
l) | Push button station / Local Control Panel near Pump a) Push Buttons (Start & Stop including emergency Stop). - 3Nos. b) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. c) The cost for fabrication panel, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 8 | No. | 3010 | #NAME? | 24080
m) | Supply and fixing of Electrolytic grade copper bus bar bus bar by means of SMC / DMC type insulator, high tensile nuts and bolts spring washers in existing panel including bending , cutting in required shape and size and colour coding with heat shrinkable PVC sleeves | 28 | Kg | 987 | #NAME? | 27636
n) | 415V PMCC Panel Board Fabrication with enclosures, earthing bus, wiring, control relays, Auxiliary contactors, Control Transformers, power contactors, Control MCBs, terminal blocks etc. All complete works. | 1 | Set | 86961 | #NAME? | 86961
10.4 | Indoor Lighting DB: Supply, Transportation, Installation, testing & Commissioning of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos DP outgoings and for 1 No 4 pole Incomer with IP-54 enclosure, bottom entry cable, necessary accessories like wiring, contactors, terminal block, aux. relays, timer etc complete. a) Incomer: 63A, TPN, MCCB and 100mA, RCCB b) Outgoings: 6-32A, DP, MCB - 8 Nos and 32A TPN MCB - 3Nos c) Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod 63A MCCB - 1No. d) Supplying, erecting & marking SPMCB 5A in provided distribution board - 3Nos. e) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. - 6Nos. f) Supplying and erecting panel mounting type digital ammeter having three and half digit LED display, external CT operated, calibrated for suitable to operate on 500V, 0 to 1000A AC supply with necessary PVC wire leads and lugs and mounting hardware on provided panel complete with calibration certificate from manufacturer.. - 1No. g) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 60/5A, 5 VA , class 1 accuracy.- 3Nos. | 2 | No. | 41716 | #NAME? | 83432
a) | The cost for fabrication panel, Copper / Al busbars, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 2 | Set | 14601 | #NAME? | 29202
10.5 | Outdoor Lighting DB
a) | Supply of Way TPN DB Horizontal with IP 43 Protection suitable for 6DP out goings and for 1 No 4 pole Incommer etc complete as per IS 8623; IS 13032; IEC 61439-3. | 2 | No. | 1527 | #NAME? | 3054
b) | Supplying, erecting & marking DPMCB 16A B- series (for lighting) in provided distribution board | 8 | No. | 1068 | #NAME? | 8544
c) | Supplying, erecting & marking TPNMCB 32A in provided distribution board | 2 | No. | 2014 | #NAME? | 4028
10.6 | Lighting system (indoor and outdoor):
a) | Supply of Lighting Luminiares
i) | Supply, transportation and fixing of 36W Recessed / Surface mounting 2' x 2' (600x600 mm) LED luminaire made of CRCA sheet housing with powder coated with acrylic diffuser, Constant current Driver as per IS: 15885 (Part 2/ Sec 13) : 2012, With System lumen output ≥3200lm operating voltage range of 150 to 265 Volts AC, P.F > 0.9, Surge protection: 2KV, THD<10%, with high power LED's having efficacy of > 120 lumins / watt, CCT: 3000K - 5700K, minimum CRI>70, .etc.,, complete. | 26 | No. | 4761 | #NAME? | 123786
ii) | Emergency Lighting: Supply & Fixing of Rechargeable emergency lamp (600 mm fluorescent lamp) or LED lamp with accessories complete | 4 | No. | 2703 | #NAME? | 10812
b) | Fixing all types and all capacities of LED fittings on the wall / ceiling / rafters / girders using 23 / 0.0076” twin twisted PVC insulated wires, required Nos of round blocks and clamps. | 48 | No. | 216 | #NAME? | 10368
c) | Supply and transportation of LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 110 lm/W and junction temprature < 70°C, with Ingrees protection IP66, Luminaire performance complies to IS 10322 (Part 5 / Sec-3), Driver surge protection 4KV, external Surge protection 10 KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete
i) | 150W | 12 | No. | 11262 | #NAME? | 135144
ii) | 60W | 10 | No. | 5018 | #NAME? | 50180
d) | Supplying and erecting street light / Peripheral light bracket for erection of single fitting made from 40 mm. dia ‗B‘ class G.I. pipe 1.0 m in length along with pole cap of 300 mm length 100 mm dia duly welded | 10 | No. | 765 | #NAME? | 7650
e) | Fabrication, Transportation and supply of hot-dip galvanized Octogonal Pole with BSEN - 10025 grade S 355 JO steel plate for shaft, IS 2062 for base plate with door opening arrangement, including the supply of suitable boards with bakelite sheet as per IS specification suitable to withstand the wind speed of 180 KMPH for 7.5 Mtrs height Pole having dimensions Bottom 130 mm,. Top 70mm with 3mm thick, base plate 220 x 220 x 12mm and 4 Nos of M20 x 700 long 'J' bolts along with template. | 12 | No. | 11225 | #NAME? | 134700
f) | Fabrication, Transportation and supply of 1 / 1.50 Mtr Length Single Arm Bracket made with MS galvanized 40mm / 50mm dia Pipe. (Pole Brackets) | 12 | No. | 1934 | #NAME? | 23208
g) | Foundation and erection charges with special T&P, for 7.5 Mtrs long Octagonal duly erecting on base plate duly providing 4 Nos foundation bolts with nuts with providing of 0.45Mtr x 0.45Mtrs x1.20 Mtr size M20 cc work vibrated concreting mixing with necessary steel (10kgs) reinforcement and curing for 7 days as directed by the field engineers during execution including excavation of Earth/BT all labour charges and cost and conveyance of materials etc.complete. | 12 | No. | 8302 | #NAME? | 99624
h) | Supply of following sizes thermo plastic cable junctions boxes IP 65 protection with metric knockouts for cable entry including threaded cable gland. (260X210X116) | 12 | No. | 1557 | #NAME? | 18684
10.7 | Supply & Installation of Earthing system
a) | Providing earth electrode of low carbon steel rod, UL listed of 17.2 mm dia, 3 Mtr long, coated with copper of 254 microns thickness, CPRI tested for short time current withstand test of 25 kA, coating thickness, environmental test (Salt Mist Test), Bend test, Tensile strength, Yield / tensile ratio, Electrical Resistivity test, complete with clamps and 2 bags of Earthplus ULTRA high grade earthing compound IEC 62561-7 complaint Eco-friendly, Maintenance free, anti corrosive, lead-free, super conductive, mineral based high-grade earthing compound, to enhance soil conductivity. With resistance <0.20 ohmsmeter, should be leach proof & sulphur free complete with earth inspection chamber of dimensions : Width : 320 mm x 320 mm, Height : 192 mm, Weight : 30 Kgs, Load bearing capacity :5000 Kgs | 4 | No. | 9489 | #NAME? | 37956
b) | Supplying and running of GI strips & GI wire for grounding connections, using necessary fixing materials as required.
i) | 32x6 mm GI Earth Strip (For 415V PMCC & Outdoor Lighting Circuit) | 400 | Mtr. | 160 | #NAME? | 64000
ii) | 25x6 mm GI Earth Strip (for Lighting panel & LDB) | 150 | Mtr. | 116 | #NAME? | 17400
iii) | 8 SWG GI Wire (Junction box, Motorised valves etc.) | 200 | Mtr. | 19 | #NAME? | 3800
10.8 | Supply & Installation of Lightning Protection System
a) | Supply of Standard / Special Mounting Structure of height 4.5 mts. pipe, and 300 x 300 x 8mm MS plate, 3 mts. 48mm OD class C GI outer pipe,1.8 mtr, 38mm OD inner pipe, for roof mounting on concrete base and with FRP adapter | 1 | No. | 18777 | #NAME? | 18777
b) | Supply and run of 25mm x 6mm GI Flat Down Condutor with necessary clamps / supports on wall / floor / ground for earth connection | 170 | Mtr. | 116 | #NAME? | 19720
c) | Supply of Test Link Box for each Down conductor in order to disconnect the earth termination system to enable measurement of resistance | 1 | No. | 4620 | #NAME? | 4620
d) | Supply and insallation maintenance free Gl Earthing System comprising of 50mm dia and 2 mtr. long earth electrode of low carbon steel rod with 100 micron bonding and 25 kgs. of carbon based environment friendly backfill compound and suitable clamp | 1 | No. | 8530 | #NAME? | 8530
10.9 | Point Wiring for lighting/fan circuits & sockets
a) | Supply of ISI marked 40mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe | 100 | Mtr. | 88 | #NAME? | 8800
b) | Supplying and erecting unbreakable concealed type modular switch box with double mounting plate for 6 module duly erected flush to wall with required chiselling and finishing with cement mortar / POP as per required to match the background. | 10 | No. | 190 | #NAME? | 1900
c) | Supply of ISI marked 25mm / 32mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe.
i) | Short point (not exceeding 3m) | 30 | Mtr. | 77 | #NAME? | 2310
ii) | Medium point above 3m and up to 6m | 50 | Mtr. | 77 | #NAME? | 3850
iii) | Long point above 6m and up to 10m | 35 | Mtr. | 77 | #NAME? | 2695
d) | Supply of 4 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 80 | Mtr. | 38 | #NAME? | 3040
e) | Supply of 2.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 380 | Mtr. | 27 | #NAME? | 10260
f) | Supply of 1.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 170 | Mtr. | 18 | #NAME? | 3060
g) | Supply & Fixing of modular switch & connected accessories on existing switch plate and enclosure
i) | 32A TPN MCB + 40A TPN RCCB (socket-Industrial Type) | 2 | No. | 8305 | #NAME? | 16610
ii) | One/Two way piano type switch 6A | 20 | No. | 92 | #NAME? | 1840
iii) | 3 pin plug socket 6A | 15 | No. | 139 | #NAME? | 2085
iv) | Piano type switch 16A | 2 | No. | 213 | #NAME? | 426
v) | 3 pin plug socket 16A | 2 | No. | 152 | #NAME? | 304
h) | Supplying and erecting five star rated energy saving Ceiling fan 230 V A.C. 50 cycles 1200 mm complete erected in position | 2 | No. | 3091 | #NAME? | 6182
10.1 | Supply, Installation, Testing and commissioning of safety procedures for Electrical Equipments as per scope, specification and drawings.
a) | Supplying and Fixing PVC synthetic elastomer electrically insulating mat with class D insulation conforming to IS:15652-2006 and CPRI tested upto 11kV | 2 | No. | 6086 | #NAME? | 12172
b) | Supplying and Erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg capacity cartridge type conform to IS 2876/15683 complete erected with necessary clamp made of 50x6 mm M.S. flat nut and bolts grouted in wall complete | 3 | No. | 11252 | #NAME? | 33756
c) | Supplying rubber gloves of 15KV conforming to IS for electrical purpose. | 2 | pairs | 1294 | #NAME? | 2588
d) | Supplying standard first aid box with necessary antiseptic cream, medicine for use on wounds due burn, crepe bandage, gauge bandage, medicated ready to use bandage (Band-Aid) adhesive tape for medicinal use, scissors, anti-septic solution, etc. (All above contents shall be of standard makes) | 1 | No. | 917 | #NAME? | 917
e) | Supplying and fixing of shock treatment chart on the wall with inside plastic sheet cover and plywood back plate frame work complete | 2 | No. | 774 | #NAME? | 1548
f) | Supplying and fixing of danger board made out of MS sheet metal with duly painted with red oxide and enamel paint. | 2 | No. | 129 | #NAME? | 258
g) | Tools and Plant
i) | Live Line Tester | 5 | No. | 92 | #NAME? | 460
ii) | Insulation Tester (Megger) 2.5kV-5kV | 1 | No. | 5911 | #NAME? | 5911
iii) | Multimeter electronic type | 2 | No. | 1183 | #NAME? | 2366
iv) | Earth Resistance Tester | 2 | No. | 7092 | #NAME? | 14184
v) | Rubber Shoes Knee Height | 3 | No. | 629 | #NAME? | 1887
vi) | DC Voltmeter range - 3V to +5V | 3 | No. | 591 | #NAME? | 1773
| TOTAL CARRIED TO BILL XB SUMMARY |  |  |  |  | 1429698
PART 2B : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
BILL OF QUANTITIES - XIB : MISCELLANEOUS WORKS
11.1 | ICA Items for City reserviors
a) | Supply, delivery at site and fixing of Electromagnetic Flow Indicating Transmitter (full bore type) with flange Ends, rates shall be inclusive of mating flanges with necessary fasteners and gaskets, as applicable and necessary.
(i) | Inlet of the reservoir, pipe size 700 mm | 1 | Nos. | 224426 | #NAME? | 224426
11.2 | Instrument & power supply cables, supplies, laying, termination & testing.
a) | Plain annealed multistranded tinned copper conductors; solid polyethylene insulation with each pair screened with aluminium-mylar tape including drain wire, with collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (2 Pair x 1.5 sq.mm) | 60 | RM | 782 | #NAME? | 46920
b) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (12 Core x 1.5 sq.mm) | 60 | RM | 1434 | #NAME? | 86040
c) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (4 Core x 1.5 sq.mm) | 20 | RM | 1141 | #NAME? | 22820
d) | Conduits and Supports (19mm OD Heavy Mechanical Stress PVC Conduit (Socketed) + Round Elbow + Circular Box (Through,Tee,Intersection,etc) + Coupler (Pipe to Pipe, End Cap) | 1 | Lot | 71627 | #NAME? | 71627
Electrical
11.3 | LT Cables
a) | Supplying, Erection & Termination of XLPE armoured cable copper conductor continuous 5.48 sq.mm. (12 SWG) GI earth wire complete erected with glands & lugs, on wall/trusses/pole or laid in provided trench/pipe as er PWD specifications.
(i) | 4C x 6 Sq.mm (LDBs, Recepacle, EOT Crane, etc.,) | 150 | Mtr. | 280 | #NAME? | 42000
(ii) | 4C x 4 Sq.mm (Street Lighting) | 400 | Mtr. | 209 | #NAME? | 83600
(iii) | 3C x 4 Sq.mm (Pumps, Valves motors, Lighting ckts, 1-ph sockets etc.,) | 500 | Mtr. | 171 | #NAME? | 85500
(iv) | 3C x 2.5 Sq.mm (Outdoor Peripheral light and Indoor Exhaust Fans) | 420 | Mtr. | 135 | #NAME? | 56700
(v) | 1 core x 2.5 sqmm, Cu. Conductor (for protective earth) | 180 | Mtr. | 7 | #NAME? | 1260
11.4 | Cable tray
a) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 300 mm width & 100 mm height comprising all required standard accessories. | 16 | Mtr. | 442 | #NAME? | 7072
b) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 150 mm width & 100 mm height comprising all required standard accessories. | 80 | Mtr. | 354 | #NAME? | 28320
11.5 | Hume pipe for Road crossings for Cable & Earth Strip crossing
a) | RCC Hume Pipe, 2000 mm Long, 150 mm Dia | 8 | No. | 223 | #NAME? | 1784
b) | Collars for RCC Hume Pipe | 4 | No. | 60 | #NAME? | 240
c) | Laying of RCC Hume pipes | 8 | No. | 33 | #NAME? | 264
11.6 | MS Chequrred plate of 6mm thick and 5.sq.meter area for trenches. | 250 | Kg | 110 | #NAME? | 27500
11.7 | Supplying and erecting exhaust fan heavy duty 440 V A.C. 50 cycles 900 RPM 375/380 mm complete erected in position. | 1 | No. | 4098 | #NAME? | 4098
| TOTAL CARRIED TO BILL XIB SUMMARY |  |  |  |  | 790171

## Summary - Singapura
CONTRACT NO. CP-13
Part 2B : CIVIL AND ELECTRO MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT SINGAPURA
SUMMARY OF BILL TOTALS
Bill No. |  | Amount in Rs.
IB | Earthworks | 269376435
IIB | Concrete and Allied works | 183897946
IIIB | General Building Works | 17630597
IVB | Water Supply & Sanitary Works | 1731986
VB | Structural Steel Works | 2000988
VIB | Roadworks | 18989726
VIIB | Pipeworks, Valves and Specials | 6744611
VIIIB | Mechanical works | 4133141
IXB | Instrumentation works | 2734085
XB | Electrical works | 1429698
XIB | Miscellaneous works | 790171
TOTAL CARRIED TO GRAND SUMMARY |  | 509459384

## Vasudevapura
BILL OF QUANTITIES
Item No. | Description | Quantity | Unit | Rate in figures (Rs.) | Rate in words (Rs.) | Amount (Rs.)
Part 2C : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - IC : EARTHWORKS
1.1 | Earthwork in excavation of foundation of structures in all types of soil excluding hard rock by mechanical means as per drawing and technical specification, including setting out, providing shoring, strutting and bracing, removal of stumps and other deleterious matter, dressing of sides and bottom, filling back the excavated earth to the extent required and utilising/transporting the remaining earth including coast of labour, materials,lead and HOM of machineries etc., complete as per specifications. | 11687 | Cum | 183 | #NAME? | 2138721
1.2 | Earthwork in excavation by manual means for structures in all types of soil excluding hard rock, including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50m after breaking of clods complete as per specifications
a) | 0 to 1.5 m depth | 485 | Cum | 438 | #NAME? | 212430
b) | 1.5 to 3 m depth | 1103 | Cum | 438 | #NAME? | 483114
c) | 3 to 4.5 m depth | 100 | Cum | 438 | #NAME? | 43800
d) | 4.5 to 6 m depth | 100 | Cum | 438 | #NAME? | 43800
1.3 | Excavation for foundation of all structures, either in pits or trenches 1.5 m and above in width, in hard rock by chiselling and / or wedging where blasting is prohibited, including stacking the excavated stuff clear from the edge of excavation with lead upto 50m including cost of explosives, labour, HOM of equipment complete as per specifications
a) | 0 to 1.5 m depth | 100 | Cum | 1093 | #NAME? | 109300
b) | 1.5 to 3 m depth | 934 | Cum | 1093 | #NAME? | 1020862
c) | 3 to 4.5 m depth | 100 | Cum | 1093 | #NAME? | 109300
d) | 4.5 to 6 m depth | 100 | Cum | 1093 | #NAME? | 109300
1.4 | Filling available excavated earth (excluding rock ) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts and including cost of all labour complete as per specifications. | 2520 | Cum | 73 | #NAME? | 183960
1.5 | Disposing off the excess excavated earth of all types within the radius of 25 km from the site by vehicle inluding loading, unloading, with all leads, lifts, labour, HOM of machinery etc., complete. | 11656 | Cum | 243 | #NAME? | 2832408
1.6 | Construction of embankment with approved material Gravel/Murrum with all lifts and leads, transporting to site, spreading, grading to required slope in uniform layers of 150mm to meet requirement complete as per specifications and drawings.(which includes cost of gravel / murrum, labour, watering charges & compaction by vibratory roller) | 1548 | Cum | 1472 | #NAME? | 2278656
1.7 | Providing and laying grass turfing on the surface of the embankment as per standards and drawings approved by the Engineer around the Ground level reservoir including cost of all labour complete as per specifications. | 1040 | sqm | 309 | #NAME? | 321360
1.8 | Dismantling of existing structures like culverts, bridges, retaining walls and other structures comprising of masonary, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary. sorting the dismantled materials, disposal of unserviceable materials, stacking the serviceable material,with all lifts complete as per specifications,
a) | Manual means: Cement concrete grade M-15 & M-20 or as directed | 10 | Cum | 2186 | #NAME? | 21860
b) | Mechanical means: Cement concrete grade M-15 & M-20 or as directed | 10 | Cum | 1458 | #NAME? | 14580
1.9 | Compaction of original ground upto 95% of proctor dry density with maximum of 6 passes of 8 to 10 tonnes power roller including filling in depression occuring during rolling including cost of all labour, HOM of machinery complete as per specifications. | 1420 | sqm | 37 | #NAME? | 52540
1.1 | Clearing and grubbing road land including uprooting rank vegetation, grass, bushes, shrubs, saplings and trees of girth upto 300mm, removal of stumps of trees cut earlier and disposal of unserviceable materials and stacking of serviceable material to be used or aunctioned, including removal and disposal of top organinc soil not exceeding 150mm in thickness complete as per specifications. By manual means.(In area of thorny jungle) | 30000 | sqm | 40 | #NAME? | 1200000
1.11 | Cutting of trees girth from 300mm to 600mm including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in the depressions / pit, labour charges complete as per specifications | 25 | Nos. | 1458 | #NAME? | 36450
1.12 | Cutting of trees girth from 600mm to 900mm including cutting of trunks, branches and removal of stumps, roots stacking of serviceable materials with all lifts and upto a lead of 1000m and earth filling in the depressions/pit, complete as per specifications | 15 | Nos. | 2186 | #NAME? | 32790
| TOTAL CARRIED TO BILL IC SUMMARY |  |  |  |  | 11245231
Part 2C : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - IIC : CONCRETE AND ALLIED WORKS
2.1 | Providing and laying in position plain cement concrete of mix 1:3:6 with OPC cement content at 220Kgs using 40 mm and down size graded granite metal course aggregates @0.84cum and the fine agregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications.
a) | Chlorine building, valve chambers,PCC filling for level difference,etc. | 122 | Cum | 6755 | #NAME? | 824110
2.2 | Providing and laying in position plain cement concrete of design mix M15 1:2:4 with OPC minimum cement content at 240Kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, shuttering, labour, HOM of machinery, curing complete as per specifications. | 516 | Cum | 6940 | #NAME? | 3581040
2.3 | Providing and laying in position reinforced cement concrete of design mix M25(Minimum cement content of 360kg/m3) as per specifications using 20 mm and down size graded granite metal course aggregates and the fine agregates with superplastisiser conforming to IS9103-1999 reaffirmed-2008, machine mixed, concrete laid in layers not exceeding 15 cms, thick, well compacted, in foundation and plinth , ground floor level for roof slabs, staircase, lintels, etc, including cost of all materials, labour, HOM of machinery, curing complete as per specifications for chlorine house and security cabin,etc. | 258 | Cum | 7912 | #NAME? | 2041296
2.4 | Providing and laying cement concrete in position reinforced cement concrete of design mix M30(Minimum cement content of 400kg/m3) as per specifications by pumping using 20 mm and down size granite Coarse aggregates & fine aggregates of ready mixed concrete (RMC) for R.C.C works laid in 15 cms thick layers and well compacted including vibrating, curing, including smooth finish in CM 1:3, with all lead and lifts etc., complete (exclusive of cost of steel and fabrication charges.) Ready Mixed Concrete for raft foundation, walls, Beams, Columns, underground chambers, baffle walls, Staircase,roof,etc., complete as per specifications. | 3785 | Cum | 8530 | #NAME? | 32286050
2.5 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons.(Type F1 finish)
a) | Reservoir,Chlorine House ,security cabin,etc., | 1385 | sqm | 729 | #NAME? | 1009665
2.6 | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 3669 | sqm | 729 | #NAME? | 2674701
b) | Level from 3.50 to 4.50m | 979 | sqm | 729 | #NAME? | 713691
c) | Level from 4.50 to 5.50m | 979 | sqm | 729 | #NAME? | 713691
d) | Level from 5.50 to 6.50m | 652 | sqm | 729 | #NAME? | 475308
2.7 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 1124 | sqm | 729 | #NAME? | 819396
b) | Level from 3.50 to 4.50m | 310 | sqm | 729 | #NAME? | 225990
c) | Level from 4.50 to 5.50m | 281 | sqm | 729 | #NAME? | 204849
d) | Level from 5.50 to 6.50m | 121 | sqm | 729 | #NAME? | 88209
e) | Level from 6.50 to 7.50m | 26 | sqm | 729 | #NAME? | 18954
2.8 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Beams Level from 0.00 to 3.50m | 333 | sqm | 729 | #NAME? | 242757
b) | Beams Level upto 4.50m | 382 | sqm | 729 | #NAME? | 278478
c) | Beams Level upto 10m | 404 | sqm | 729 | #NAME? | 294516
2.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs, landing, balconies and likes thickness upto 200 mm including cost of all materials, labours, complete as per specifications. (Type F2 finish)
a) | Reservoir, Chlorine house,security cabin,etc., | 3085 | sqm | 729 | #NAME? | 2248965
2.1 | Providing TMT bars of Fe 500(CRS) grade steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 382 | MT | 71308 | #NAME? | 27239656
2.11 | Providing TMT bars of Fe500 grade steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 28 | MT | 67665 | #NAME? | 1894620
2.12 | Fabricating and supplying anchor bolts, pipe sleeves, channels, angles, plates and all other types of inserts in concrete members and placing them in position as specified on drawings at all locations and at all levels including two coats of approved oil paint over one coat of zinc-rich primer over exposed surfaces. | 1020 | kg | 108 | #NAME? | 110160
2.13 | Filling of box-outs left in RCC walls, etc after erection of pipes, inserts in reinforced concrete of grade M30 with coarse aggregate of size 20 mm downgraded, including roughening and preparing internal surfaces of box-outs, adding expansive agents to concrete, shuttering for Class F2 finish, compacting, curing, finishing etc complete but excluding reinforcement wherever specified.
a) | For M30 grade concrete (Minimum cement content of 400kg/m3) | 198 | Cum | 9511 | #NAME? | 1883178
| TOTAL CARRIED TO BILL IIC SUMMARY |  |  |  |  | 79869280
Part 2C : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - IIIC : GENERAL BUILDING WORKS
3.1 | Providing and laying 230 mm thick rubble packing in plinth with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, including spreading 12 mm layer of stone grit on top, etc., complete for all building works as per drawings, details and specifications. | 98 | sqm | 713 | #NAME? | 69874
3.2 | Providing and constructing precast concrete solid blocks with compressive strength not less than 35kg. per sqm with cement mortar 1:4 masonry (quoin, Jamb, closer blocks) with solid concrete blocks of size 40X20X20 cms conforming to IS.2185/ 1965 in superstructure including cost of materials, labour charges, double scaffolding, curing complete as per specifications. | 703 | sqm | 1454 | #NAME? | 1022162
3.3 | Providing plastering to masonry including providing and removing double scaffolding rounding of all corners whever required smooth rendering curing etc., complete as per specifications with burnt brick masonry plain plastering 20mm thick in CM 1:4 (external) | 801 | sqm | 336 | #NAME? | 269136
3.4 | Providing plastering to masonry including providing and removing scaffolding rounding of all corners whever required, smooth rendering curing etc complete as per specifications with burnt brick masonry plain plastering 12mm thick in CM 1:4 with lime rendering (internal) | 1071 | sqm | 283 | #NAME? | 303093
3.5 | Providing and finishing external walls in two coats with waterproof cement paint and primer of approved brand and shade to give an even shade after throughly brooming the surface to remove all dirt and loose powdered material, free from mortar drops and other foreign matter cost of materials, labour, complete as per specifications.
a) | Reservoir,Chlorine House and watchman cabin,etc | 3329 | sqm | 175 | #NAME? | 582575
3.6 | Providing and applying painting in two coats with plastic emulsion paint and primer of approved brand on wall surface to give an even approved shade after thoroughly brushing the surface, free from mortor drops and other foreign matter including preparing the surface even and sand paper smooth, cost of materials, labour, complete as per specifications.
a) | Chlorine House and security cabin,etc | 817 | sqm | 178 | #NAME? | 145426
3.7 | Providing and laying flooring and steps fine machined polished granite stone slabs of approved colour 20mm thick on cement mortar bed 1:6, 20mm thick, and, joints finished with cement mortar 1:3 over existing cement concrete bed ,including cost of materials, labour, curing complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin,etc | 37 | sqm | 4372 | #NAME? | 161764
3.8 | Providing and fixing skirting of 300mm high using prepolished water cut/gang saw of 19mm thick grey granite 0.5mm wide chamfered width and depth and fixing in CM 1:4 of 20mm thick after chipping the walls, etc., including cost of all materials, mortar,labour,curing,etc., complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin,etc | 36 | RM | 1312 | #NAME? | 47232
3.9 | Providing dado, rises of steps with colour glazed tiles on 10mm thick cement plaster 1:3 and jointed with white cement slurry over rough plaster surface ( excluding cost of rough plastered surface which should be measured and paid separately) using glazed tiles of approved make and size including cost of materials, labour, complete as per specifications.
a) | chlorine house, reservoir staircase,etc | 22 | sqm | 1299 | #NAME? | 28578
3.1 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tiles of approved make and colour of size 100 mm x 200 mm x 20 mm thick for flooring, on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Neutralization pit, walls and base slab | 38 | sqm | 4070 | #NAME? | 154660
3.11 | Providing and laying M-15 cement concrete flooring, 60mm thick with metallic concrete hardner topping, under layer of 45mm thick M-15 cement concrete using broken granite metal of 20mm and downsize and top layer of 15mm thick metallic cement hardner consisting of mix 1:2 by volume, with metallic hardening compound of approved quality mix in the ratio of 4:1, including finishing, cost of materials, labour, curing, complete as per specifications.
a) | Drum room and chlorinator room | 134 | sqm | 886 | #NAME? | 118724
3.12 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tile dado of approved make and colour of size 100 mm x 200 mm x 20 mm thick for on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Drum room and chlorinator room | 20 | sqm | 4070 | #NAME? | 81400
3.13 | Providing and fixing ceramic tiles (non skid) of size 400x400mm for flooring laid on a bed of 20mm thick cement mortar 1:3 mix flush pointing with white cement mixed with matching colour pigment including curing, cleaning,etc., complete.The work includes cost of all materials,mortar,labour charges for all items of work,hire charges for equipment,etc., complete as per specifications.
a) | Wash room of control and Office rooms | 80 | sqm | 1325 | #NAME? | 106000
3.14 | Providing, fabricating and fixing in position anodised aluminum doors using following aluminum sections mat or glossy finish, outer frame of section 101.6 x 44.45 x 3.18 mm at 2.404 Kg/m, door shutters vertical section - 44.62 x 44.45 x 3.00mm at 1.426 Kg/m, bottom section 114.3 x 44.45 x 3.18mm at 2.646 kg/m, top section 47.62 x 44.45 x 3.00mm at 1.426 kg/m, middle section 49.91 x 44.45 x 3.00mm at 1.495 Kg/m, glazing clips 19 x 17.3x 11mm x 0.90 mm thick at 0.124 kg/m, all sections anodised to 12 to 15 microns. Cut to length, joint mitred corners grinded, shutters pivoted opening arrangement with h eavy duty aluminum alloy automatic door closer, floor mounted, providing and fixing standard approved accessories such as aluminum handle, for full width or length, tower bolts, lock pivots, PVC or rubber gaskets with 5.5 mm thick plain glass for top and bottom panel, aluminum sections treated for removal of rust, coated with greasy material for non adherence of mortar or any sticky material, the assembled frame fitted with corner angles, strips and fitted with rawl plugs, or teak wood gutties, to RCC columns, or masonry sides, including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. as per specifications | 20 | sqm | 9472 | #NAME? | 189440
3.15 | Providing, fabricating and fixing in position Stainless steel doors including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. | 4 | sqm | 36429 | #NAME? | 145716
3.16 | Providing and fixing mechanical gear type rolling shutters of approved make out of 18 guage, 75mm wide cold rolled steel laths of convex corrugation, with side guides and bottom rail, with interlocking arrangements for steel laths by means of alternate clips, suspension shaft with High tension coil type springs two numbers, mounted on specially designed pipe shaft, with bracket plates, guide channels, ball bearing arrangements, for inside & outside locking complete including pulling hooks, 4Nos. handles with all fittings and accessories, painted with a coat of red lead paint (without top cover) cost of materials, labour, HOM of machinery complete as per specifications. | 21 | sqm | 7286 | #NAME? | 153006
3.17 | Providing and fixing hydraulic door closures -Aluminium body | 5 | Nos. | 2915 | #NAME? | 14575
3.18 | Providing and fixing mortice door lock heavy duty to doors. | 9 | Nos. | 2186 | #NAME? | 19674
3.19 | Providing and fixing in position anodized aluminium windows and ventilators as per approved drawings with sliding shutters using double track window frame section of size 61.85x31.75mm. with 1.2mm thick, bottom section weight 0.695 kg/m, sides and top sections 1.3 mm. thick weight 0.659 kg/m; and shutter comprising top and bottom section of size 40mmx18mm, 1.25mm thick 0.417 kg./m; shutter outer side 40mmx18mm, 1.25mm.thick weight 0.417 kg/m, shutter interlock section 40mmx26.7mm, 1.1mm thick, weight 0.469 kg/m. the shutters mounted on nylon rollers with approved quality of fixtures such as aluminium handles tower bolts etc.; and providing and fixing 5.5mm. thick plain glass for shutters fitted with rubber beading aluminium sections anodised 12 to 15 microns, including cutting to required length, joints mitred subdividing the frame tenonned and rivetted in the assembled frame stiffened with end clips at corners angles etc., and fixed to the walls, lintels, floor beams/cills as the case may be with necessary steel screws, raul plugs, or teak wood gatties including cutting masonry or concrete and making good the original surface using cement mortar, aluminium sections pretreated for removal of any rust and protection of further rust formation and coated with the greasy materials for non- adhesion of mortar and any other sticky materials, (this coating should be cleaned after installation) including cost of all materials, fixtures, labour and HOM of machinery complete as per specifications. | 50 | sqm | 7286 | #NAME? | 364300
3.2 | Providing, fabricating, assembling and fixing in position aluminium partitions with aluminium section anodized to 12-15 microns using sections in combination of plain, single grove and double grove as per requirements for the frames of overall size 101.6mm x 44.45mm, 3.18mm.thick having section weight, plain sections 2.40kg/m single grove section 2.541kg/m. and double grovesection 2.683 kg/m and bottom 46 kg/m; aluminium louvres of size 77.6mmx27.6mm 1.7mm. thick section weight 0.483kg/m; bottom portions provided with 12mm. thick prelaminated sheet both side of approved colour lamination exterior grade; aluminium sections of mat finish or glossy finish using section, spacing of vertical member shall not exceed 0.6 m. c to c; sections are cut to the required lengths, joints mitered and corners grinded subdividing frames tennoned and rivetted to the frames, the assembled frame should be stiffened with corner angles stripped and fixed with screws, rawl plugs and teak wood gutties to R.C.C.columns or masonry on sides, R.C.C. lintels or beams at top and floor at bottom, including cutting chistling and making good with cement mortar to match the surface, providing and fixing bottom panel filled with the materials to a height of 0.9m. from floor level; and 5.5mm. thick plain glass for middle portion viz., 0.9m. to 2.13 m. and top panel with lower sections, the glass and panels fitted with glazing clips of 19mmx17.3mm. with thickness of 0.9mm. weight 0.124kg/m; aluminium sections pre-treated for removal of any rust and prevention of further rust formation, and coated with greasy materials for non-adherence of mortars or any other sticky materials; vertical members embedded in the flooring by making suitable size holes and fixing with cement mortar, with necessary opening for fixing of doors of standard size including cost of materials, fixtures, labour and HOM of machinery complete. | 17 | sqm | 9472 | #NAME? | 161024
3.21 | Providing and fixing 225 mm wide and minimum 6 mm thick continuous PVC waterstops of approved quality at contraction and expansion joints as per manufacturer's instructions at all levels for Ground level reservoir. | 2133 | RM | 365 | #NAME? | 778545
3.22 | Supplying and fixing PVC encapsulated CI rungs to shapes and at locations specified in drawings and specifications for Valve chambers | 50 | kg | 108 | #NAME? | 5400
3.23 | Providing and fixing 10 gauge aluminium sheet to required shape and size with rawl plugs and screws to concrete curbs to cover up expansion joints at roof level, including filling the notch with bitumen as specified in drawing, for Ground level reservoir. | 30 | sqm | 2264 | #NAME? | 67920
3.24 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant Type A) in a groove of size 15 mm x 20 mm deep at contraction joints including forming groove as specified on drawing for Ground level reservoir. | 1800 | RM | 387 | #NAME? | 696600
3.25 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant type B) in a groove of size 25 mm x 20 mm deep at expansion joints including forming groove as specified on drawing for Ground level reservoir. | 50 | RM | 401 | #NAME? | 20050
3.26 | Providing and fixing in position 25 mm thick sellotex board/filler compound as per standards and approved by the Engineer, of required sizes at expansion joints as specified in drawing for Ground level reservoir. | 180 | sqm | 328 | #NAME? | 59040
3.27 | Providing and laying 500 gauge polyethylene sheet of approved make and quality on blinding layer and wherever specified as directed by Engineer, for Ground level reservoir. | 2869 | sqm | 62 | #NAME? | 177878
3.28 | Providing and fixing slip-strip (1 mm thick PVC sheet) of approved quality or equivalent at junction between top of wall and bottom of roof slab in two layers as directed by Engineer, for Ground level reservoir. | 75 | sqm | 729 | #NAME? | 54675
3.29 | Providing and laying in position yelahanka tiles of size 125 x 250mm of approved quality and make, over a bed of cement mortar 1:3 with thickness varying from 100mm to 25mm including weather proof course and pointed with cement mortar 1:3 mix with red oxide including curing cost of materials, labour complete as per specifications. | 4000 | sqm | 1403 | #NAME? | 5612000
3.3 | Providing and fixing 150 mm diameter cast iron air ventilators as per design & shape indicated in drawings over roof slab of all reservoirs with mosquito proof jali etc complete. | 40 | Nos. | 6896 | #NAME? | 275840
3.31 | Installing precast circular hume pipe septic tank suitable for 5 persons capacity conforming to IS 2470, and constructing standard soak pit for the same capacity, including excavation and backfilling of pit, PVC Pipe, filling soakpit with broken bricks, overflow connection precast RC slab and construction of manhole chamber with cover, C.I. vent pipe with cowl and connecting it to incoming and outgoing pipelines etc., complete. | 1 | Nos. | 145713 | #NAME? | 145713
3.32 | Supplying of and application of food grade epoxy painting on the inside surface of GLR headroom, GLR inside staircase and wall face at staircase complete, as per applicable Technical specification clause, including all labour, HOM of equipment, lead, lifts taxes etc., complete, including all surface preparation, testing, Rate shall be inclusive of all materials, tools and plants, testing and inspection etc., complete. | 100 | sqm | 481 | #NAME? | 48100
3.33 | Providing and laying M15 grade plain concrete in screed for required level above base slab of reservoir to specified slope with coarse aggregate of size 10mm downgraded including formwork and compacting with a hand rammer,curing,finishing,etc., complete as per specifications. | 420 | Cum | 6871 | #NAME? | 2885820
3.34 | Providing and laying plain cement concrete of design mix M15 with OPC minimum cement content at 240kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers with thickness varying from 150mm to 75mm over 230 mm thick rubble packing with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, etc., complete for plinth protection 1m wide as per drawings, details and specifications. | 75 | RM | 1689 | #NAME? | 126675
| TOTAL CARRIED TO BILL IIIC SUMMARY |  |  |  |  | 15092615
Part 2C : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - IVC : WATER SUPPLY AND SANITARY WORKS
4.1 | Providing and fixing white vitreous china clay, water closet European type (Pedestal type, P-trap) with black solid plastic seat and lid, CP brass hinges, rubber buffers, 10 litre low level, P.V.C flushing cistern (all are approved make) with fittings, SS brackets, 40mm diameter flush bend with fittings and clamps, overflow arrangements with specials and 25mm mosquito proof coupling of approved design, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 14572 | #NAME? | 29144
4.2 | Providing and fixing white vitreous china clay, flat back wash basins of size 550 mm x 400 mm with a pair of 15mm C.P brass pillar taps with SS brackets, 32mm C.P brass waste of standard pattern, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 8743 | #NAME? | 17486
4.3 | Providing and fixing white vitreous china clay, flat back, lipped front urinal basin of 430x260x350mm in the range of three with 7.5 litres PVC automatic flushing cistern, SS brackets, standard flush pipe and C.P brass spreaders with brass unions and G.I clamps painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 7286 | #NAME? | 14572
4.4 | Providing and fixing in position brass bib cock of aproved quality 15mm nominal bore including cost of all materials, labour and HOM of equipments with all leads complete as per specifications. | 3 | Nos. | 1458 | #NAME? | 4374
4.5 | Providing brick masonry inspection chambers, rectangular in size 90 cm x 45 cm and upto 1.5 m depth on sewer line , with 230 mm brick wall in cement mortar (1:2), plastered both inside and outside with 20 mm thick cement mortar (1:2),including 1.6 m x 1.2 m x 290 mm thick cement concrete 1:2:4 in haunches as per standard plan including excavation, backfilling the excavated sides and removing surplus earth and with heavy duty C.I. cover and frame and with M.S. steps fixed in cement mortar with cement and sand filleting. | 2 | Nos. | 26223 | #NAME? | 52446
4.6 | Same as in for item 4.5 above but for depth greater than 1.5 m and upto 3 m | 2 | Nos. | 38907 | #NAME? | 77814
4.7 | Constructing circular type manhole 1500mm internal dia at bottom, 525mm dia at top, in wire cut burnt brick masonry with 1:5 cement mortar, cement plaster 1:3, finish with a floating coat of neat cement, RCC 1:2:4 top slab using 20mm and downsize granite metal, foundation concrete, M7.5 using 40mm and downsize granite metal and making channels in cement concrete M15 using 20mm and downsize granite metal, neatly finished curing, fixing CI cover complete including external, footrests and 12mm thick cement plaster on the external surface, cost of materials, labour charges, HOM of machineries complete as per specifications. | 2 | Nos. | 75964 | #NAME? | 151928
4.8 | Providing and fixing PVC Nahani trap of approved make conforming to ISI specifications and construction of cistern in M-15 as per directions. (rate inclusive of cost of materials and fixtures and conveyance of materials to work spot). | 3 | Nos. | 875 | #NAME? | 2625
4.9 | Providing stoneware gully trap of approved quality and make fixing in M-15 and plastering with CM 1:3 wherever necessary. (rate includes cost of all materials, fixtures and lead). With 100mm outlet. | 2 | Nos. | 1458 | #NAME? | 2916
4.1 | Providing and fixing 75 mm dia PVC slotted vent cowls conforming to IS 3989 with necessary fixtures and as directed by Engineer. | 2 | Nos. | 729 | #NAME? | 1458
4.11 | Providing and fixing white glazed 'P' trap as per IS 2556 (Part 7) 100 mm dia with SS grating 10 mm thick etc., complete. | 1 | Nos. | 1458 | #NAME? | 1458
4.12 | Providing and fixing cast copper alloy stop valves, polished bright, conforming to and as per IS 781.
a) | 25 mm dia. | 1 | Nos. | 729 | #NAME? | 729
b) | 20 mm dia. | 2 | Nos. | 729 | #NAME? | 1458
c) | 15 mm dia. | 1 | Nos. | 729 | #NAME? | 729
4.13 | Providing and fixing SS towel rail 740mm length, 20mm dia with C.P brackets, fixed to wooden cleats with C.P brass screws including cost of materials, labour complete as per specifications. | 4 | Nos. | 2186 | #NAME? | 8744
4.14 | Providing and fixing best quality SS liquid soap bottle holders of approved make with SS brackets, screws, rawl plugs, etc. complete. | 3 | Nos. | 1458 | #NAME? | 4374
4.15 | Providing and fixing 600x450 bevellead edge mirror of superior glass with 6mm hard board backing and fixed to wooden cleats with C.P screws, washers, including cost of materials, labour complete as per specifications. | 4 | Nos. | 7286 | #NAME? | 29144
4.16 | Providing and fixing white glazed partition walls of size 825 mm x 450 mm x 25 mm as per IS 2556 (Part 6 ) of approved make, properly supported with C.I. brackets, etc. complete. | 2 | Nos. | 2911 | #NAME? | 5822
4.17 | Providing and fixing UPVC water pipes and fittings 'B' class pressure rating of 10kg/cm2 conforming to IS 13592 and IS14735, with all necessary fixtures and bends, including testing the line as specified,etc.,complete.
a) | 25 mm dia. | 100 | RM | 292 | #NAME? | 29200
b) | 20 mm dia. | 25 | RM | 219 | #NAME? | 5475
c) | 15 mm dia. | 10 | RM | 146 | #NAME? | 1460
4.18 | Providing and Fixing PVC soil waste and vent pipes 100 mm diameter - 10kg/cm2 with spun yarn soaked in cement slurry and cement mortar 1:2 including cost of materials, labour, testing complete as per specifications. | 200 | RM | 875 | #NAME? | 175000
4.19 | Providing and fixing PVC pipes of approved make and 150 mm dia - 10kg/cm2 conforming to IS 651, including all necessary fixtures and bends, including excavation, backfilling, testing etc., complete as per specification. | 200 | RM | 1284 | #NAME? | 256800
4.2 | Providing and fixing 100 mm dia - 10kg/cm2 PVC rain water pipes as per IS: 4984 including all fixtures such as brackets, bends etc.as directed by the Engineer. | 765 | RM | 315 | #NAME? | 240975
4.21 | Providing and fixing cast iron bell mouth rain water outlets including MS grating, etc., complete as directed by Engineer.
a) | 100mm Dia. | 90 | Nos. | 1458 | #NAME? | 131220
4.22 | Providing, supplying and fixing rectangular SS manhole covers with chains connecting to the frame of size 1200x900 and 900mm x 600mm of grade 304L for roof slab of reservoir and underground chambers at locations shown in drawing including SS frame etc. complete. | 750 | kg | 583 | #NAME? | 437250
4.23 | Supplying PVC pipes conforming to IS 4985:2000 with latest amendments and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations and cuts of pipes wherever necessary including jointing of PVC and specials with jointing of approved type, with all labour with all lead & lifting. (75mm dia - 10kg/cm2) | 65 | RM | 729 | #NAME? | 47385
| TOTAL CARRIED TO BILL IVC SUMMARY |  |  |  |  | 1731986
Part 2C : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - VC : STRUCTURAL STEELWORKS
5.1 | Supplying, fabricating, delivering to site, loading, unloading, etc. and erecting structural steel work for the following works, including one shop coat of red oxide zinc chromate primer after fabrication and one coat of the same after erection and two coats of synthetic enamel paint of approved shade, etc. complete as per specifications.
a) | Chlorine house | 350 | kg | 108 | #NAME? | 37800
5.2 | Providing and fixing in position MS ladders as per drawing, including painting etc. complete. | 191 | kg | 117 | #NAME? | 22347
5.3 | Providing and fixing 304- grade Stainless steel handrails of 14 gauge pipe for ramps or staircase are made out of stainless steel hollow pipes, using 50mm dia for verticals @ 1.60mtr c/c are fixed to the rams or steps by drilling with bolts and 100mm dia MS base plates 10mm gauge for fixing of vertical pipes 4 nos anchor bolts & 40mm dia pipes are fixed horizontally for 2 rows top one pipe are fixed with vertical pipes another one are fixed with elbows & 25mm dia pipes are fixed horizontally for 2 rows with elbow top measure @ equal intervals including cutting, welding, bending wherever necessary with suitable caps @ tops, bottoms, corners finishing with mat/shining etc., completeincluding cost and conveyance of all materials, labour for all items of work, HOM of euipment with all lead and lift, loading and unloading, transportation charges and all other incidental charges etc., complete as per specification and directions of the Engineer-in-charge of the work. Ramps or staircase for physically challenged. | 246 | RM | 2889 | #NAME? | 710694
5.4 | Providing and fixing MS frame with 10 mm thick flats with grating cover with stiffeners for openings as specified in drawing at all locations and levels, including painting, etc., complete. | 1935 | kg | 108 | #NAME? | 208980
| TOTAL CARRIED TO BILL VC SUMMARY |  |  |  |  | 979821
Part 2C : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - VIC : ROADWORKS
ROADS & DRAINS
6.1 | Construction of Granular sub-base for 200 mm by providing coarse graded material , spreading in uniform layers on prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density, complete as per clause 401 for Grading-v of MORTH V Specifications. | 322 | Cum | 2851 | #NAME? | 918022
6.2 | Providing, laying, spreading and compacting 150 mm graded stone aggregate to Wet Mix Macadam (WMM) specification including premixing the material with water at OMC in mechanical mix plant carriage of mixed material by tipper to site, laying in uniform layers in sub base/ base course on well prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density. MORTH clause 406 | 241 | Cum | 3078 | #NAME? | 741798
6.3 | Providing and applying Primer Coat with bitumen emulsion using emulsion pressure distributor at the rate of 0.60 kg per sqm on the prepared WMM surface including cleaning of WMM surface and spraying primer using mechanical spray jet as per MORTH V specification clause No. 502 complete in all respects. | 1072 | sqm | 34 | #NAME? | 36448
6.4 | Providing and applying Tack Coat on the prepared WMM surface hot bitumen primed at 1Kg per Sqm heating bitumen in boiler fitted with spray set as per MORTH V specification clause No. 503 complete in all respect. | 1072 | sqm | 57 | #NAME? | 61104
6.5 | Providing and laying Bituminous Macadam 50 mm thick from 100-120TPH hot mix plant using crushed aggregates of specified grading premixed with bituminous binder, transported to site, laid over a previously prepared surface to the required grade, level and alignment and rolled by virbratory roller as per MORTH V specification clauses 505 to achieve the desired compaction complete with all lead and lift and direction of Engineer-in-charge. | 54 | Cum | 10448 | #NAME? | 564192
6.6 | Providing and applying Tack Coat on the prepared BM surface at 0.5Kg / Sqm heating bitumen in boiler fitted with spray set as per specification clause No. 503 of MORTH V complete in all respects. | 1072 | sqm | 28 | #NAME? | 30016
6.7 | Providing and laying Semi Dense Bituminous Concrete(SDBM) 25 mm thick with 100-120 TPH hot mix plant using crushed aggregates of specified grading, premixed with bituminous binder 5.4 to 5.6 per cent of mix and filler, transporting the hot mix to work site, laying with a hydrostatic paver finisher with mechanical control to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause No. 508 complete with all lead and lift, with 60/70 Grade bitumen and direction of Engineer-in-charge. | 32 | Cum | 11361 | #NAME? | 363552
6.8 | Construction of covered drain 0.3m x 0.45m (inside dimensions) with RCC M20 grade 10cm thick for walls and floor, laid over 10cm thick 1:3:6 PCC bed and covered with M30 grade RCC slab 0f 15cm thick excluding earth work including reinforcement @ 35 kg/rmt and form work complete as per specifications. | 536 | RM | 5724 | #NAME? | 3068064
COMPOUND WALL
6.9 | Earthwork excavation for foundation in all types of soil excluding hard rock including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50 m and disposal of excess excavated earth including all leads and lifts after breaking of clods complete as per specifications.
a) | 0 -1.5m | 1244 | Cum | 152 | #NAME? | 189088
6.10 | Providing and laying in position plain cement concrete of mix M10 with OPC cement @220kgs, with 20mm and down size graded granite metal coarse aggregates @ 0.84cum and fine aggregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms thick, well compacted, in foundation and plinth including cost of all materials, labour, HOM of machinery curing complete as per specifications. | 44 | Cum | 6409 | #NAME? | 281996
6.11 | Filling available excavated earth (excluding rock) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts including cost of labour complete as per specifications. | 400 | Cum | 73 | #NAME? | 29200
6.12 | Providing and laying in position Reinforced Cement Concrete of Grade M25 (Design mix) with 20mm and downsize graded granite metal machine mixed, concrete laid in layers not exceeding 15 cm thick, vibrated for R.C.C. beams, columns of all sizes in foundation, plinth and superstructure ground floor levels of roof slabs, base slab, staircases, lintels, columns including cost of all materials, labour, HOM of machinary, curing, complete as per specifications. | 145 | Cum | 7617 | #NAME? | 1104465
6.13 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for foundation, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specifications | 1560 | sqm | 729 | #NAME? | 1137240
6.14 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per speciications. | 690 | sqm | 729 | #NAME? | 503010
6.15 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications | 50 | sqm | 729 | #NAME? | 36450
6.16 | Providing TMT Steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, tying with binding wire and anchoring to the adjoining members whenever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinary complete as per specifications. (Fe 500 grade confirm to IS 1786). | 20 | MT | 69122 | #NAME? | 1382440
6.17 | Providing barbed fixed 12x12 guage drawn into stone pillar or iron pillars including drawing in holes wherever necessary excluding the cost of pillar but including the cost of barbed wire and binding wire etc., complete | 268 | RM | 132 | #NAME? | 35376
6.18 | M.S Angle | 450 | kg | 108 | #NAME? | 48600
6.19 | Providing and finishing external walls in two coats with waterproof paint with primer of approved brand and shade to give an even shade after thoroughly brooming the surface to remove all dirt and loose powdered material free from mortar drops and other foreign matter cost of materials, labour complete as per specifications | 1615 | sqm | 175 | #NAME? | 282625
6.20 | Supplying and fixing M.S rectangular poles made out of 2 equal angles of 65x65x6 mm welded together and fixed in CC (1:2:4) with 2 nos 16mm dia MS hold fast rods each of length 25cms including cost of all materials cutting,bending,scaffolding wherever necessary,nicely finishing the welded joints with all lead lifts and as per specifications including providing 2 coats of approved quality paint over one coat of shop painting. | 1570 | RM | 1337 | #NAME? | 2099090
6.21 | Providing chain link fencing 50mm size of 8 guage properly stretched between rectangular poles and fixed with suitable bolts & nuts, the free ends shall be welded to the pole and block pipe at top and bottom as required including cost of all materials, labour, lead and lifts and as per the directions of the Engineer in-charge of work including two coats of approved quality paint over one coat of shop paint. | 980 | sqm | 365 | #NAME? | 357700
6.22 | Providing and fixing MS block pipe of 38mm dia of heavy guage of 14 including removing the bends, cutting the pipe, and fixing pipe in between the two vertical poles (MS rectangular poles) and spot welding the chain linkwith MS block pipe including cost of all materials wastage in cutting, scaffolding wherever necessary with all lead and lift,etc., complete including two coats of approved quality paint over one coat of shop paint. | 500 | RM | 209 | #NAME? | 104500
6.23 | Providing and erecting in position., 2400x600x60 mm thk precast slab panels of M25 grade reinforced cement concrete including reinforcement and formwork with coarse aggregate of size 20mm downgraded with minimum cement content of 320kg/cum. The reinforcement consists of 1 no of 10mm dia loop and round the panel, 5 nos of 8mm dia horizontals and 15 nos of 8mm dia verticals equally spaced. The thickness of the panel shall be 60mm thick at the middle and 70mm thick at the edges for a width of 250mm.The gaps between the panels shall be packed with 1:4 cement mortar and the final surface between the panel and RCC post shall be finished using silicon sealant of approved make, complete as per specification & drawing.
a) | For both side plain finished panels of 2400mm x 600mm size, as shown in the drawings. | 135 | Nos. | 3524 | #NAME? | 475740
b) | For one side plain and other side with horizontal grooves as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 135 | Nos. | 3524 | #NAME? | 475740
c) | For one side plain and other side with vertical grooves as as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 135 | Nos. | 3524 | #NAME? | 475740
d) | For one side plain and other side with BWSSB logo as per the pattern panels of 2400mm x 600mm size, as shown in the drawings. | 135 | Nos. | 3524 | #NAME? | 475740
6.24 | Providing and fixing gates consisting of 40 mm NB light glass GI pipes external framework and 8 x 30 MS flats internal framework with 16 guage MS jointing plates and tack welded over the framework with necessary hinges and locking arrangement, including painting over approved primer coat, etc. all complete as per specifications and drawings. | 2 | MT | 107603 | #NAME? | 215206
| TOTAL CARRIED TO BILL VIC SUMMARY |  |  |  |  | 15493142
Part 2C : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - VIIC : PIPEWORKS, VALVES AND SPECIALS
Pipelines, Specials and Appurtenances
7.1 | Providing, Fabricating, shop welding, transporting, handling, aligning, laying and jointing / welding of MS pipes of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate also include loading and unloading, radiography of joints as specified and hydraulic testing of pipeline to specified pressure as per specifications and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings.
a) | 800 mm internal diameter with 6 mm shell thickness overflow pipe of GLR | 15 | RM | 9306 | #NAME? | 139590
b) | 700 mm internal diameter with 6 mm shell thickness Inlet pipe of GLR | 15 | RM | 8152 | #NAME? | 122280
c) | 1000 mm internal diameter with 7 mm shell thickness Outlet pipe of GLR | 15 | RM | 13565 | #NAME? | 203475
7.2 | Providing, fabricating, shop welding, handling, transporting, aligning, laying and jointing of MS specials of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate include loading and unloading, radiography of joints as specified and hydraulic testing of specials to specified pressure and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings. | 1200 | kg | 139 | #NAME? | 166800
7.3 | Providing guniting (CM 1:3 over 50 x 50 mm weld mesh of 13 gauge) on the external surface of pipes and specials including supplying and fixing reinforcement as per specifications after cleaning the pipes including curing etc., at fabrication yard and guniting the field joints at site between two pipes after testing complete in all respects as per specifications.
a) | 813 mm OD pipes and specials, 25 mm thick guniting | 38 | Sq.m | 729 | #NAME? | 27702
b) | 712 mm OD pipes and specials, 25 mm thick guniting | 33 | Sq.m | 729 | #NAME? | 24057
c) | 1015 mm OD pipes and specials, 25 mm thick guniting | 48 | Sq.m | 729 | #NAME? | 34992
7.4 | Providing food grade internal epoxy lining of 0.5 mm thick as per specifications to the internal surfaces of mild steel pipeline, fittings, specials etc., including surface preparation, machine lining, curing and testing / inspection etc., complete.
a) | 800 mm ID pipes & specials to 800 mm finished diameter, 0.5 mm thick internal epoxy lining | 36 | Sq.m | 583 | #NAME? | 20988
b) | 700 mm ID pipes & specials to 700 mm finished diameter, 0.5 mm thick internal epoxy lining | 31 | Sq.m | 583 | #NAME? | 18073
c) | 1000 mm ID pipes & specials to 1000 mm finished diameter, 0.5 mm thick internal epoxy lining | 46 | Sq.m | 583 | #NAME? | 26818
7.5 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Manually operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 700 mm dia PN 16 for 700 mm ID | 1 | Nos. | 576799 | #NAME? | 576799
b) | 1000 mm dia PN 16 for 1000 mm ID | 1 | Nos. | 1142167 | #NAME? | 1142167
7.6 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Motorised operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 700 mm dia PN 16 for 700 mm ID | 2 | Nos. | 686789 | #NAME? | 1373578
b) | 1000 mm dia PN 16 for 1000 mm ID | 2 | Nos. | 1334649 | #NAME? | 2669298
7.7 | Supply,installation, testing & Commissioning of (Scour purpose) Ductile Iron (DI) Resilient seated soft sealing sluice valve. Detailed Valve specifications & arrangement shall be as defined in Volume 2. The rate is inclusive of cost of mating flanges, valve,bolts & nuts and rubber insertions,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 300 mm dia. PN 16 size scour valves for GLR | 2 | Nos. | 55047 | #NAME? | 110094
7.8 | Providing, supplying and fixing SS 304 Expansion Bellows with Flange Ends as per specifications and drawings.Detailed Specifications & arrangement shall be as defined in Volume 2. The rate shall include transportation to site with all leads and lifts, aligning and jointing approved anti-corrosive paint etc., complete in all aspects. Rates are incluisve of Labour Charges.
a) | 700 mm dia.PN 16 | 3 | Nos. | 125765 | #NAME? | 377295
b) | 1000 mm dia. PN 16 | 3 | Nos. | 185128 | #NAME? | 555384
7.9 | Providing and laying following dia of MS pipes conforming to IS 3589 in trenches outside the pipeline scour valve chambers for draining, include lining & coating, excavation, connecting to scour valve, backfilling the earth etc., complete.
a) | 300 mm dia. 5.6 mm thick | 60 | RM | 3294 | #NAME? | 197640
| TOTAL CARRIED TO BILL VIIC SUMMARY |  |  |  |  | 7787030
Part 2C : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - VIIIC : MECHANICAL WORKS
8.1 | Mechanical Equipment
a) | Supply,Testing, Installation & Commissioing of 2 Kg/hr Capacity with 0-2 ppm dosage level Vaccum type Chlorination System 2 sets.(1W+1S) with all allied works complete as per Bid specification of Volume 2
(i) | 2 Kg/hr | 2 | Sets. | 1621047 | #NAME? | 3242094
b) | Supplying,Testing, Installation & Commissioing of Chlorine gas Filled Chlorine Tonners of 900 Kgs with all allied works complete as per Bid specification of Volume 2 | 2 | Nos. | 189426 | #NAME? | 378852
c) | Supply,Testing, Installation & Commissioing of Electrically operated wire rope hoist of 2 Ton capacity conforming to IS 3938 for chlorine house with suitable I-Beam arrangement and Electrical Panels etc.with all allied works complete as per Bid specification of Volume 2 | 1 | Nos. | 291461 | #NAME? | 291461
d) | Service Water Network system
(i) | Providing, erecting and giving test of Centrifugal Monoblock Pump set conforming to IS 9079 operating at 1500 RPM with pump casing: Cast Iron IS 210 FG Gr.260, Impeller:Bronze IS 318 LTB2, Shaft:SS 410 , Pump Seal: Mechanical Seal, priming funnel, cock, suitable flanges at suction and delivery side. Pump shall have common shaft for pump and motor. Motor shall be suitable for working on 2.0 HP, 415 V + 10%, 3 Ph, 50Hz+/-5% A.C. Supply. Motor shall be TEFC type. Pump set shall be suitable for working at various discharge and head requirements. Pump shall be erected on Provided C.C. foundation block with suitable foundation bolts grouted in C.C foundation block. | 2 | Nos. | 56935 | #NAME? | 113870
(ii) | Pressure Gauge: Supply, delivery at site and fixing of glycerine filled stainless steel pressure gauge of 100 mm Dia. suitable for the above pump sets with nipple, stop cock and three way cock for cleaning and necessary length of SS tubing suitable for mounting on the suction and delivery of pump, including 15 NB isolating valve etc., complete with all lead and lifts etc, complete as per specification | 2 | Nos. | 1909 | #NAME? | 3818
(iii) | Providing and fixing in position brass gate valve with CI wheel (screwed end) 40 mm nominal bore including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 6 | Nos. | 8109 | #NAME? | 48654
(iv) | Providing and fixing in position 40 mm nominal bore non-return valve vertical type of approved make including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 2 | Nos. | 8960 | #NAME? | 17920
(v) | Providing & Fixing to wall,ceiling and floor high density polyethylene pipes 6.00 Kgf/sq.cm working pressure of outside diameter raising mains & exposed distribution pipes with special flange, compression type fittings, wall clips, making good the wall, ceiling and floor, including cost of all materials, labour charges, HOM and testing complete as per specifications.
i | 40 mm dia | 125 | RM | 219 | #NAME? | 27375
(vi) | Providing and placing on terrace,polyethylene water storage tanks with manhole lid and suitable locking arrangements,making holes of suitable diameter for inlet,outlet and overflow pipes,including cost of all materials,labour transportation charges,HOM of equipments and testing complete as per specifications (for 1000 litres capacity) within the GLR Campus. | 1 | Nos. | 14572 | #NAME? | 14572
| TOTAL CARRIED TO BILL VIIIC SUMMARY |  |  |  |  | 4138616
Part 2C : INSTRUMENTATION WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - IXC : INSTRUMENTATION WORKS
9.1 | ICA Items for City reserviors
a) | Designing, Supplying, Installing, commissioning & testing of Ultrasonic level transmitter with following technical parameters at GLR and Interfacing with PLC panel including all required Mounting accessories, factory testing & inspection complete as per specifications. Range : (0 - 10 m) | 2 | Nos. | 62344 | #NAME? | 124688
b) | Supply, delivery at site and fixing of Conductivity type Level Switch (back up to level transmitter), High Level & Low Level sensing - (4point contact) with necessary instrumentation cabling,glands with suitable stub and flange and bolting arrangement for hook-up, as applicable and necessary, factory testing & inspection. Range : (0 - 10 m) | 2 | Nos. | 78049 | #NAME? | 156098
c) | Design, Supply, Installation, Testing of Residual chlorine analyzer at GLR and Interfacing with PLC panel and factory testing for complete functional test & inspection. | 1 | Nos. | 227160 | #NAME? | 227160
9.2 | Instrument & power supply cables, supplies, laying, termination & testing.
a) | Plain annealed multistranded tinned copper conductors; solid polyethylene insulation with each pair screened with aluminium-mylar tape including drain wire, with collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (2 Pair x 1.5 sq.mm) | 200 | RM | 782 | #NAME? | 156400
b) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (12 Core x 1.5 sq.mm) | 200 | RM | 1434 | #NAME? | 286800
c) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (4 Core x 1.5 sq.mm) | 290 | RM | 1141 | #NAME? | 330890
d) | Conduits and Supports (19mm OD Heavy Mechanical Stress PVC Conduit (Socketed) + Round Elbow + Circular Box (Through,Tee,Intersection,etc) + Coupler (Pipe to Pipe, End Cap) | 1 | Lot | 71627 | #NAME? | 71627
| TOTAL CARRIED TO BILL IXC SUMMARY |  |  |  |  | 1353663
Part 2C : ELECTRICAL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - XC: ELECTRICAL WORKS
LT Electrical Works for GLR Premises
10.1 | Supplying and erecting four pole metal clad ON LOAD change over switch 415V, 125A erected on angle iron /GI frame approved make complete. | 1 | No. | 10257 | #NAME? | 10257
10.2 | Supply, Transportation, loading/unloading, Laying, Installation & Commissioning of Solid Aluminum conductor up to 10 sqmm balance stranded conductor, XLPE Insulated, cores laid up, PVC tape/Extruded Innersheathed for Multicore Cables , Armour (Aluminium wire for single core up to 70 sqmm balance Aluminium strip, Glavanised wire for cables upto 2x10 sqmm, 3x10 sqmm,4x6 sqmm balance all galvanised steel strip), extruded PVC Type ST2 sheathed, 650/1100V grade as per IS 7098(Part 1) 1988, Incoming Cable from nearst 415V overhead line as per ESCOM specifications a) Metering Box to Change Over Switch b) Change Over Switch to 415V Panel Board
a) | 3.5C x 50sq.mm (Al. Conductor) | 100 | Mtr. | 263 | #NAME? | 26300
b) | 3.5C x 50sq.mm (Al. Conductor) - Glands | 4 | No. | 98 | #NAME? | 392
c) | 3.5C x 50sq.mm (Al. Conductor) - Lugs | 16 | No. | 50 | #NAME? | 800
10.3 | 415V PMCC Panel Board (Including Chlorine MCC): Supply, Transportation, Installation, Testing & Commissioning of 415V LT Board of cubicle type with 415V, 50 Hz, 3 PH, TPN, 25 kA for 1 sec, wtih IP-54 enclosure with Bottom entry, consisting of incoming and outgoing feeders with metering and protection with complete accessories as per specification and single line diagram.
a) | Incomer: 125A, 25kA, 4P, MCCB | 1 | No. | 10850 | #NAME? | 10850
b) | Outgoing: 25A TPN MPCB (Motorised Valves) | 4 | No. | 4307 | #NAME? | 17228
c) | Outgoing: 63A TPN MCCB (Indoor Lighting DB 1 & 2, Spare 2Nos.) | 4 | No. | 9074 | #NAME? | 36296
d) | Outgoing: 32A TPN MCCB (2T Crane, Spare 2Nos.) | 3 | No. | 7112 | #NAME? | 21336
e) | Supplying & erecting LED type indicating pilot lamp with LED colours red , yellow and blue, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 1 | Set | 1697 | #NAME? | 1697
f) | Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 34 | No. | 566 | #NAME? | 19244
g) | Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod upto 250A MCCB | 8 | No. | 1465 | #NAME? | 11720
h) | Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 100/5A, 5 VA , class 1 accuracy | 3 | No. | 625 | #NAME? | 1875
i) | Multi Functions Meters - Flush type for M V Panel Board LED type, CT/PT, Voltage, Current, Frequency, Kilowatt, Kilo Volt Ampere, KVAR , KVAH, Run Hours, unbalance(V,A),Rpm, Phase angles,Thd-Class 1 With RS 485 Port | 1 | No. | 10390 | #NAME? | 10390
j) | Supplying, erecting & marking SPMCB 5A in provided distribution board | 3 | No. | 571 | #NAME? | 1713
k) | DOL Feeder a) 25A MPCB - 1No b) Supplying and erecting D.O.L. Starter 400V. 3 phase, 50 cycles with no volt coil and overload element with necessary materials and connected to supply upto 7.5 H.P. - 1No. c)Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. d) Supplying, fixing and wiring 0 to 30amps Ammeter Analog SR 65 5D/5A C.T.operated-AC - 1No. e) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 30/5A, 5 VA , class 1 accuracy - 1No. | 8 | No. | 8943 | #NAME? | 71544
l) | Push button station / Local Control Panel near Pump a) Push Buttons (Start & Stop including emergency Stop). - 3Nos. b) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. c) The cost for fabrication panel, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 8 | No. | 3010 | #NAME? | 24080
m) | Supply and fixing of Electrolytic grade copper bus bar bus bar by means of SMC / DMC type insulator, high tensile nuts and bolts spring washers in existing panel including bending , cutting in required shape and size and colour coding with heat shrinkable PVC sleeves | 28 | Kg | 987 | #NAME? | 27636
n) | 415V PMCC Panel Board Fabrication with enclosures, earthing bus, wiring, control relays, Auxiliary contactors, Control Transformers, power contactors, Control MCBs, terminal blocks etc. All complete works. | 1 | Set | 86961 | #NAME? | 86961
10.4 | Indoor Lighting DB: Supply, Transportation, Installation, testing & Commissioning of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos DP outgoings and for 1 No 4 pole Incomer with IP-54 enclosure, bottom entry cable, necessary accessories like wiring, contactors, terminal block, aux. relays, timer etc complete. a) Incomer: 63A, TPN, MCCB and 100mA, RCCB b) Outgoings: 6-32A, DP, MCB - 8 Nos and 32A TPN MCB - 3Nos c) Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod 63A MCCB - 1No. d) Supplying, erecting & marking SPMCB 5A in provided distribution board - 3Nos. e) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. - 6Nos. f) Supplying and erecting panel mounting type digital ammeter having three and half digit LED display, external CT operated, calibrated for suitable to operate on 500V, 0 to 1000A AC supply with necessary PVC wire leads and lugs and mounting hardware on provided panel complete with calibration certificate from manufacturer.. - 1No. g) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 60/5A, 5 VA , class 1 accuracy.- 3Nos. | 2 | No. | 41716 | #NAME? | 83432
a) | The cost for fabrication panel, Copper / Al busbars, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 2 | Set | 14601 | #NAME? | 29202
10.5 | Outdoor Lighting DB
a) | Supply of Way TPN DB Horizontal with IP 43 Protection suitable for 6DP out goings and for 1 No 4 pole Incommer etc complete as per IS 8623; IS 13032; IEC 61439-3. | 2 | No. | 1527 | #NAME? | 3054
b) | Supplying, erecting & marking DPMCB 16A B- series (for lighting) in provided distribution board | 8 | No. | 1068 | #NAME? | 8544
c) | Supplying, erecting & marking TPNMCB 32A in provided distribution board | 2 | No. | 2014 | #NAME? | 4028
10.6 | Lighting system (indoor and outdoor):
a) | Supply of Lighting Luminiares
i) | Supply, transportation and fixing of 36W Recessed / Surface mounting 2' x 2' (600x600 mm) LED luminaire made of CRCA sheet housing with powder coated with acrylic diffuser, Constant current Driver as per IS: 15885 (Part 2/ Sec 13) : 2012, With System lumen output ≥3200lm operating voltage range of 150 to 265 Volts AC, P.F > 0.9, Surge protection: 2KV, THD<10%, with high power LED's having efficacy of > 120 lumins / watt, CCT: 3000K - 5700K, minimum CRI>70, .etc.,, complete. | 26 | No. | 4761 | #NAME? | 123786
ii) | Emergency Lighting: Supply & Fixing of Rechargeable emergency lamp (600 mm fluorescent lamp) or LED lamp with accessories complete | 4 | No. | 2703 | #NAME? | 10812
b) | Fixing all types and all capacities of LED fittings on the wall / ceiling / rafters / girders using 23 / 0.0076” twin twisted PVC insulated wires, required Nos of round blocks and clamps. | 43 | No. | 216 | #NAME? | 9288
c) | Supply and transportation of LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 110 lm/W and junction temprature < 70°C, with Ingrees protection IP66, Luminaire performance complies to IS 10322 (Part 5 / Sec-3), Driver surge protection 4KV, external Surge protection 10 KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete
i) | 150W | 9 | No. | 11262 | #NAME? | 101358
ii) | 60W | 8 | No. | 5018 | #NAME? | 40144
d) | Supplying and erecting street light / Peripheral light bracket for erection of single fitting made from 40 mm. dia ‗B‘ class G.I. pipe 1.0 m in length along with pole cap of 300 mm length 100 mm dia duly welded | 8 | No. | 765 | #NAME? | 6120
e) | Fabrication, Transportation and supply of hot-dip galvanized Octogonal Pole with BSEN - 10025 grade S 355 JO steel plate for shaft, IS 2062 for base plate with door opening arrangement, including the supply of suitable boards with bakelite sheet as per IS specification suitable to withstand the wind speed of 180 KMPH for 7.5 Mtrs height Pole having dimensions Bottom 130 mm,. Top 70mm with 3mm thick, base plate 220 x 220 x 12mm and 4 Nos of M20 x 700 long 'J' bolts along with template. | 9 | No. | 11225 | #NAME? | 101025
f) | Fabrication, Transportation and supply of 1 / 1.50 Mtr Length Single Arm Bracket made with MS galvanized 40mm / 50mm dia Pipe. (Pole Brackets) | 9 | No. | 1934 | #NAME? | 17406
g) | Foundation and erection charges with special T&P, for 7.5 Mtrs long Octagonal duly erecting on base plate duly providing 4 Nos foundation bolts with nuts with providing of 0.45Mtr x 0.45Mtrs x1.20 Mtr size M20 cc work vibrated concreting mixing with necessary steel (10kgs) reinforcement and curing for 7 days as directed by the field engineers during execution including excavation of Earth/BT all labour charges and cost and conveyance of materials etc.complete. | 9 | No. | 8302 | #NAME? | 74718
h) | Supply of following sizes thermo plastic cable junctions boxes IP 65 protection with metric knockouts for cable entry including threaded cable gland. (260X210X116) | 9 | No. | 1557 | #NAME? | 14013
10.7 | Supply & Installation of Earthing system
a) | Providing earth electrode of low carbon steel rod, UL listed of 17.2 mm dia, 3 Mtr long, coated with copper of 254 microns thickness, CPRI tested for short time current withstand test of 25 kA, coating thickness, environmental test (Salt Mist Test), Bend test, Tensile strength, Yield / tensile ratio, Electrical Resistivity test, complete with clamps and 2 bags of Earthplus ULTRA high grade earthing compound IEC 62561-7 complaint Eco-friendly, Maintenance free, anti corrosive, lead-free, super conductive, mineral based high-grade earthing compound, to enhance soil conductivity. With resistance <0.20 ohmsmeter, should be leach proof & sulphur free complete with earth inspection chamber of dimensions : Width : 320 mm x 320 mm, Height : 192 mm, Weight : 30 Kgs, Load bearing capacity :5000 Kgs | 4 | No. | 9489 | #NAME? | 37956
b) | Supplying and running of GI strips & GI wire for grounding connections, using necessary fixing materials as required.
i) | 32x6 mm GI Earth Strip (For 415V PMCC & Outdoor Lighting Circuit) | 300 | Mtr. | 160 | #NAME? | 48000
ii) | 25x6 mm GI Earth Strip (for Lighting panel & LDB) | 150 | Mtr. | 116 | #NAME? | 17400
iii) | 8 SWG GI Wire (Junction box, Motorised valves etc.) | 200 | Mtr. | 19 | #NAME? | 3800
10.8 | Supply & Installation of Lightning Protection System
a) | Supply of Standard / Special Mounting Structure of height 4.5 mts. pipe, and 300 x 300 x 8mm MS plate, 3 mts. 48mm OD class C GI outer pipe,1.8 mtr, 38mm OD inner pipe, for roof mounting on concrete base and with FRP adapter | 1 | No. | 18777 | #NAME? | 18777
b) | Supply and run of 25mm x 6mm GI Flat Down Condutor with necessary clamps / supports on wall / floor / ground for earth connection | 125 | Mtr. | 116 | #NAME? | 14500
c) | Supply of Test Link Box for each Down conductor in order to disconnect the earth termination system to enable measurement of resistance | 1 | No. | 4620 | #NAME? | 4620
d) | Supply and insallation maintenance free Gl Earthing System comprising of 50mm dia and 2 mtr. long earth electrode of low carbon steel rod with 100 micron bonding and 25 kgs. of carbon based environment friendly backfill compound and suitable clamp | 1 | No. | 8530 | #NAME? | 8530
10.9 | Point Wiring for lighting/fan circuits & sockets
a) | Supply of ISI marked 40mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe | 100 | Mtr. | 88 | #NAME? | 8800
b) | Supplying and erecting unbreakable concealed type modular switch box with double mounting plate for 6 module duly erected flush to wall with required chiselling and finishing with cement mortar / POP as per required to match the background. | 10 | No. | 190 | #NAME? | 1900
c) | Supply of ISI marked 25mm / 32mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe.
i) | Short point (not exceeding 3m) | 30 | Mtr. | 77 | #NAME? | 2310
ii) | Medium point above 3m and up to 6m | 50 | Mtr. | 77 | #NAME? | 3850
iii) | Long point above 6m and up to 10m | 35 | Mtr. | 77 | #NAME? | 2695
d) | Supply of 4 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 80 | Mtr. | 38 | #NAME? | 3040
e) | Supply of 2.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 380 | Mtr. | 27 | #NAME? | 10260
f) | Supply of 1.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 170 | Mtr. | 18 | #NAME? | 3060
g) | Supply & Fixing of modular switch & connected accessories on existing switch plate and enclosure
i) | 32A TPN MCB + 40A TPN RCCB (socket-Industrial Type) | 2 | No. | 8305 | #NAME? | 16610
ii) | One/Two way piano type switch 6A | 20 | No. | 92 | #NAME? | 1840
iii) | 3 pin plug socket 6A | 15 | No. | 139 | #NAME? | 2085
iv) | Piano type switch 16A | 2 | No. | 213 | #NAME? | 426
v) | 3 pin plug socket 16A | 2 | No. | 152 | #NAME? | 304
h) | Supplying and erecting five star rated energy saving Ceiling fan 230 V A.C. 50 cycles 1200 mm complete erected in position | 2 | No. | 3091 | #NAME? | 6182
10.1 | Supply, Installation, Testing and commissioning of safety procedures for Electrical Equipments as per scope, specification and drawings.
a) | Supplying and Fixing PVC synthetic elastomer electrically insulating mat with class D insulation conforming to IS:15652-2006 and CPRI tested upto 11kV | 2 | No. | 6086 | #NAME? | 12172
b) | Supplying and Erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg capacity cartridge type conform to IS 2876/15683 complete erected with necessary clamp made of 50x6 mm M.S. flat nut and bolts grouted in wall complete | 3 | No. | 11252 | #NAME? | 33756
c) | Supplying rubber gloves of 15KV conforming to IS for electrical purpose. | 2 | pairs | 1294 | #NAME? | 2588
d) | Supplying standard first aid box with necessary antiseptic cream, medicine for use on wounds due burn, crepe bandage, gauge bandage, medicated ready to use bandage (Band-Aid) adhesive tape for medicinal use, scissors, anti-septic solution, etc. (All above contents shall be of standard makes) | 1 | No. | 917 | #NAME? | 917
e) | Supplying and fixing of shock treatment chart on the wall with inside plastic sheet cover and plywood back plate frame work complete | 2 | No. | 774 | #NAME? | 1548
f) | Supplying and fixing of danger board made out of MS sheet metal with duly painted with red oxide and enamel paint. | 2 | No. | 129 | #NAME? | 258
g) | Tools and Plant
i) | Live Line Tester | 5 | No. | 92 | #NAME? | 460
ii) | Insulation Tester (Megger) 2.5kV-5kV | 1 | No. | 5911 | #NAME? | 5911
iii) | Multimeter electronic type | 2 | No. | 1183 | #NAME? | 2366
iv) | Earth Resistance Tester | 2 | No. | 7092 | #NAME? | 14184
v) | Rubber Shoes Knee Height | 3 | No. | 629 | #NAME? | 1887
vi) | DC Voltmeter range - 3V to +5V | 3 | No. | 591 | #NAME? | 1773
| TOTAL CARRIED TO BILL XC SUMMARY |  |  |  |  | 1302014
Part 2C : CIVIL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
BILL OF QUANTITIES - XIC : MISCELLANEOUS WORKS
11.1 | ICA Items for City reserviors
a) | Supply, delivery at site and fixing of Electromagnetic Flow Indicating Transmitter (full bore type) with flange Ends, rates shall be inclusive of mating flanges with necessary fasteners and gaskets, as applicable and necessary.
(i) | Inlet of the reservoir, pipe size 700 mm | 1 | Nos. | 224426 | #NAME? | 224426
11.2 | Miscellaneous Instruments
a) | Designing.supplying, Installing commissioning & testing of Surge Protection Devices | 6 | Nos. | 32558 | #NAME? | 195348
b) | Designing,supplying, Installing commissioning & testing of online UPS with AC Distribution Board(Min 5 KvA Industrial UPS with 60 min backup on full load of field instrumentation and control equipment inclusive of communication equipment to transfer data to CSC) and factory testing & inspection. | 1 | Nos. | 14650 | #NAME? | 14650
c) | supplying, Installing commissioning & testing of Junction Boxes | 4 | Nos. | 18279 | #NAME? | 73116
d) | supplying, Installing commissioning & testing of Field Instrument enclosures-IP 65 rated for all field instruments. | 7 | Nos. | 8954 | #NAME? | 62678
11.3 | Automation System
a) | Designing.supplying, Installing commissioning & testing of hot standby PLC with 16" colour HMI to control valves and to monitor the level and flow in the facility with required SCADA software.HMI shall be color with touchscreen functionality for complete auto operationm with FAT & SAT as per Contract requirements.(also include integration of flowmeter data (flowmeter’s which has been installed under other contracts) with the PLC based control system for continuous monitoring of both incoming and outgoing flow data at each location. All required cabling for connection, required hardware (splitters) with the PLC based control system shall be integral part of scope of work under this contract) | 1 | Nos. | 1074393 | #NAME? | 1074393
b) | Designing, supplying, installing, commissioning & testing of CCTV IR water proof camera suitable for upto 100ft.with IR Dome camera, control key board, DVR, Hard Disk, cables, UPT transreceivers etc. complete. (Close Circuit Television System to be installed at the reservoir locations to cover all areas of the facilities) and factory testing & SAT. | 4 | Nos. | 26866 | #NAME? | 107464
Electrical
11.4 | LT Cables
a) | Supplying, Erection & Termination of XLPE armoured cable copper conductor continuous 5.48 sq.mm. (12 SWG) GI earth wire complete erected with glands & lugs, on wall/trusses/pole or laid in provided trench/pipe as er PWD specifications.
(i) | 4C x 6 Sq.mm (LDBs, Recepacle, EOT Crane, etc.,) | 150 | Mtr. | 280 | #NAME? | 42000
(ii) | 4C x 4 Sq.mm (Street Lighting) | 320 | Mtr. | 209 | #NAME? | 66880
(iii) | 3C x 4 Sq.mm (Pumps, Valves motors, Lighting ckts, 1-ph sockets etc.,) | 540 | Mtr. | 171 | #NAME? | 92340
(iv) | 3C x 2.5 Sq.mm (Outdoor Peripheral light and Indoor Exhaust Fans) | 400 | Mtr. | 135 | #NAME? | 54000
(v) | 1 core x 2.5 sqmm, Cu. Conductor (for protective earth) | 180 | Mtr. | 7 | #NAME? | 1260
11.5 | Cable tray
a) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 300 mm width & 100 mm height comprising all required standard accessories. | 16 | Mtr. | 442 | #NAME? | 7072
b) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 150 mm width & 100 mm height comprising all required standard accessories. | 75 | Mtr. | 354 | #NAME? | 26550
11.6 | Hume pipe for Road crossings for Cable & Earth Strip crossing
a) | RCC Hume Pipe, 2000 mm Long, 150 mm Dia | 8 | No. | 223 | #NAME? | 1784
b) | Collars for RCC Hume Pipe | 4 | No. | 60 | #NAME? | 240
c) | Laying of RCC Hume pipes | 8 | No. | 33 | #NAME? | 264
11.7 | MS Chequrred plate of 6mm thick and 5.sq.meter area for trenches. | 250 | Kg | 110 | #NAME? | 27500
11.8 | Supplying and erecting exhaust fan heavy duty 440 V A.C. 50 cycles 900 RPM 375/380 mm complete erected in position. | 1 | No. | 4098 | #NAME? | 4098
| TOTAL CARRIED TO BILL XIC SUMMARY |  |  |  |  | 2076063

## Summary - Vasudevapura
CONTRACT NO. CP-13
Part 2C : CIVIL AND ELECTRO MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT VASUDEVPURA
SUMMARY OF BILL TOTALS
Bill No. |  | Amount in Rs.
IC | Earthworks | 11245231
IIC | Concrete and Allied works | 79869280
IIIC | General Building Works | 15092615
IVC | Water Supply & Sanitary Works | 1731986
VC | Structural Steel Works | 979821
VIC | Roadworks | 15493142
VIIC | Pipeworks, Valves and Specials | 7787030
VIIIC | Mechanical works | 4138616
IXC | Instrumentation works | 1353663
XC | Electrical works | 1302014
XIC | Miscellaneous works | 2076063
TOTAL CARRIED TO GRAND SUMMARY |  | 141069461

## Chokkanahalli
BILL OF QUANTITIES
Item No. | Description | Quantity | Unit | Rate in figures (Rs.) | Rate in words (Rs.) | Amount (Rs.)
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - ID : EARTHWORKS
1.1 | Earthwork in excavation of foundation of structures in all types of soil excluding hard rock by mechanical means as per drawing and technical specification, including setting out, providing shoring, strutting and bracing, removal of stumps and other deleterious matter, dressing of sides and bottom, filling back the excavated earth to the extent required and utilising/transporting the remaining earth including coast of labour, materials,lead and HOM of machineries etc., complete as per specifications. | 19412 | Cum | 183 | #NAME? | 3552396
1.2 | Earthwork in excavation by manual means for structures in all types of soil excluding hard rock, including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50m after breaking of clods complete as per specifications
a) | 0 to 1.5 m depth | 4796 | Cum | 438 | #NAME? | 2100648
b) | 1.5 to 3 m depth | 262 | Cum | 438 | #NAME? | 114756
c) | 3 to 4.5 m depth | 100 | Cum | 438 | #NAME? | 43800
d) | 4.5 to 6 m depth | 100 | Cum | 438 | #NAME? | 43800
1.3 | Excavation for foundation of all structures, either in pits or trenches 1.5 m and above in width, in hard rock by chiselling and / or wedging where blasting is prohibited, including stacking the excavated stuff clear from the edge of excavation with lead upto 50m including cost of explosives, labour, HOM of equipment complete as per specifications
a) | 0 to 1.5 m depth | 100 | Cum | 1093 | #NAME? | 109300
b) | 1.5 to 3 m depth | 2205 | Cum | 1093 | #NAME? | 2410065
c) | 3 to 4.5 m depth | 100 | Cum | 1093 | #NAME? | 109300
d) | 4.5 to 6 m depth | 100 | Cum | 1093 | #NAME? | 109300
1.4 | Filling available excavated earth (excluding rock ) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts and including cost of all labour complete as per specifications. | 2883 | Cum | 73 | #NAME? | 210459
1.5 | Disposing off the excess excavated earth of all types within the radius of 25 km from the site by vehicle inluding loading, unloading, with all leads, lifts, labour, HOM of machinery etc., complete. | 21185 | Cum | 243 | #NAME? | 5147955
1.6 | Construction of embankment with approved material Gravel/Murrum with all lifts and leads, transporting to site, spreading, grading to required slope in uniform layers of 150mm to meet requirement complete as per specifications and drawings.(which includes cost of gravel / murrum, labour, watering charges & compaction by vibratory roller) | 3132 | Cum | 1472 | #NAME? | 4610304
1.7 | Providing and laying grass turfing on the surface of the embankment as per standards and drawings approved by the Engineer around the Ground level reservoir including cost of all labour complete as per specifications. | 2208 | sqm | 309 | #NAME? | 682272
1.8 | Dismantling of existing structures like culverts, bridges, retaining walls and other structures comprising of masonary, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary. sorting the dismantled materials, disposal of unserviceable materials, stacking the serviceable material,with all lifts complete as per specifications,
a) | Manual means: Cement concrete grade M-15 & M-20 or as directed | 140 | Cum | 2186 | #NAME? | 306040
b) | Mechanical means: Cement concrete grade M-15 & M-20 or as directed | 140 | Cum | 1458 | #NAME? | 204120
1.9 | Compaction of original ground upto 95% of proctor dry density with maximum of 6 passes of 8 to 10 tonnes power roller including filling in depression occuring during rolling including cost of all labour, HOM of machinery complete as per specifications. | 2850 | sqm | 37 | #NAME? | 105450
1.1 | Clearing and grubbing road land including uprooting rank vegetation, grass, bushes, shrubs, saplings and trees of girth upto 300mm, removal of stumps of trees cut earlier and disposal of unserviceable materials and stacking of serviceable material to be used or aunctioned, including removal and disposal of top organinc soil not exceeding 150mm in thickness complete as per specifications. By manual means.(In area of thorny jungle) | 19250 | sqm | 40 | #NAME? | 770000
1.11 | Cutting of trees girth from 300mm to 600mm including cutting of trunks, branches and removal of stumps stacking of serviceable materials, earth filling in the depressions / pit, labour charges complete as per specifications | 100 | Nos. | 1458 | #NAME? | 145800
1.12 | Cutting of trees girth from 600mm to 900mm including cutting of trunks, branches and removal of stumps, roots stacking of serviceable materials with all lifts and upto a lead of 1000m and earth filling in the depressions/pit, complete as per specifications | 50 | Nos. | 2186 | #NAME? | 109300
| TOTAL CARRIED TO BILL ID SUMMARY |  |  |  |  | 20885065
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - IID : CONCRETE AND ALLIED WORKS
2.1 | Providing and laying in position plain cement concrete of mix 1:3:6 with OPC cement content at 220Kgs using 40 mm and down size graded granite metal course aggregates @0.84cum and the fine agregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications.
a) | Chlorine building, valve chambers,PCC filling for level difference,etc. | 155 | Cum | 6755 | #NAME? | 1047025
2.2 | Providing and laying in position plain cement concrete of design mix M15 1:2:4 with OPC minimum cement content at 240Kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, shuttering, labour, HOM of machinery, curing complete as per specifications. | 1989 | Cum | 6940 | #NAME? | 13803660
2.3 | Providing and laying in position reinforced cement concrete of design mix M25(Minimum cement content of 360kg/m3) as per specifications using 20 mm and down size graded granite metal course aggregates and the fine agregates with superplastisiser conforming to IS9103-1999 reaffirmed-2008, machine mixed, concrete laid in layers not exceeding 15 cms, thick, well compacted, in foundation and plinth , ground floor level for roof slabs, staircase, lintels, etc, including cost of all materials, labour, HOM of machinery, curing complete as per specifications for chlorine house and security cabin,etc. | 284 | Cum | 7912 | #NAME? | 2247008
2.4 | Providing and laying cement concrete in position reinforced cement concrete of design mix M30(Minimum cement content of 400kg/m3) as per specifications by pumping using 20 mm and down size granite Coarse aggregates & fine aggregates of ready mixed concrete (RMC) for R.C.C works laid in 15 cms thick layers and well compacted including vibrating, curing, including smooth finish in CM 1:3, with all lead and lifts etc., complete (exclusive of cost of steel and fabrication charges.) Ready Mixed Concrete for raft foundation, walls, Beams, Columns, underground chambers, baffle walls, Staircase,roof,etc., complete as per specifications. | 15374 | Cum | 8530 | #NAME? | 131140220
2.5 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons.(Type F1 finish)
a) | Reservoir,Chlorine House ,security cabin,etc., | 7520 | sqm | 729 | #NAME? | 5482080
2.6 | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 13411 | sqm | 729 | #NAME? | 9776619
b) | Level from 3.50 to 4.50m | 3375 | sqm | 729 | #NAME? | 2460375
c) | Level from 4.50 to 5.50m | 3375 | sqm | 729 | #NAME? | 2460375
d) | Level from 5.50 to 6.50m | 2180 | sqm | 729 | #NAME? | 1589220
2.7 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Level from 0.00 to 3.50m | 8190 | sqm | 729 | #NAME? | 5970510
b) | Level from 3.50 to 4.50m | 2328 | sqm | 729 | #NAME? | 1697112
c) | Level from 4.50 to 5.50m | 2304 | sqm | 729 | #NAME? | 1679616
d) | Level from 5.50 to 6.50m | 1131 | sqm | 729 | #NAME? | 824499
e) | Level from 6.50 to 7.50m | 43 | sqm | 729 | #NAME? | 31347
2.8 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications. (Type F2 finish)
a) | Beams Level from 0.00 to 3.50m | 386 | sqm | 729 | #NAME? | 281394
b) | Beams Level upto 4.50m | 360 | sqm | 729 | #NAME? | 262440
c) | Beams Level upto 10m | 435 | sqm | 729 | #NAME? | 317115
2.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs, landing, balconies and likes thickness upto 200 mm including cost of all materials, labours, complete as per specifications. (Type F2 finish)
a) | Reservoir, Chlorine house,security cabin,etc., | 12295 | sqm | 729 | #NAME? | 8963055
2.1 | Providing TMT bars of Fe 500(CRS) grade steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 1741 | MT | 71308 | #NAME? | 124147228
2.11 | Providing TMT bars of Fe500 grade steel reinforcement for R.C.C work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps, hooks and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 34 | MT | 67665 | #NAME? | 2300610
2.12 | Fabricating and supplying anchor bolts, pipe sleeves, channels, angles, plates and all other types of inserts in concrete members and placing them in position as specified on drawings at all locations and at all levels including two coats of approved oil paint over one coat of zinc-rich primer over exposed surfaces. | 850 | kg | 108 | #NAME? | 91800
2.13 | Filling of box-outs left in RCC walls, etc after erection of pipes, inserts in reinforced concrete of grade M30 with coarse aggregate of size 20 mm downgraded, including roughening and preparing internal surfaces of box-outs, adding expansive agents to concrete, shuttering for Class F2 finish, compacting, curing, finishing etc complete but excluding reinforcement wherever specified.
a) | For M30 grade concrete (Minimum cement content of 400kg/m3) | 315 | Cum | 9511 | #NAME? | 2995965
| TOTAL CARRIED TO BILL IID SUMMARY |  |  |  |  | 319569273
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - IIID : GENERAL BUILDING WORKS
3.1 | Providing and laying 230 mm thick rubble packing in plinth with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, including spreading 12 mm layer of stone grit on top, etc., complete for all building works as per drawings, details and specifications. | 68 | sqm | 713 | #NAME? | 48484
3.2 | Providing and constructing precast concrete solid blocks with compressive strength not less than 35kg. per sqm with cement mortar 1:4 masonry (quoin, Jamb, closer blocks) with solid concrete blocks of size 40X20X20 cms conforming to IS.2185/ 1965 in superstructure including cost of materials, labour charges, double scaffolding, curing complete as per specifications. | 965 | sqm | 1454 | #NAME? | 1403110
3.3 | Providing plastering to masonry including providing and removing double scaffolding rounding of all corners whever required smooth rendering curing etc., complete as per specifications with burnt brick masonry plain plastering 20mm thick in CM 1:4 (external) | 982 | sqm | 336 | #NAME? | 329952
3.4 | Providing plastering to masonry including providing and removing scaffolding rounding of all corners whever required, smooth rendering curing etc complete as per specifications with burnt brick masonry plain plastering 12mm thick in CM 1:4 with lime rendering (internal) | 1405 | sqm | 283 | #NAME? | 397615
3.5 | Providing and finishing external walls in two coats with waterproof cement paint and primer of approved brand and shade to give an even shade after throughly brooming the surface to remove all dirt and loose powdered material, free from mortar drops and other foreign matter cost of materials, labour, complete as per specifications.
a) | Reservoir,Chlorine House and watchman cabin,etc. | 8469 | sqm | 175 | #NAME? | 1482075
3.6 | Providing and applying painting in two coats with plastic emulsion paint and primer of approved brand on wall surface to give an even approved shade after thoroughly brushing the surface, free from mortor drops and other foreign matter including preparing the surface even and sand paper smooth, cost of materials, labour, complete as per specifications.
a) | Chlorine House and security cabin,etc. | 1152 | sqm | 178 | #NAME? | 205056
3.7 | Providing and laying flooring and steps fine machined polished granite stone slabs of approved colour 20mm thick on cement mortar bed 1:6, 20mm thick, and, joints finished with cement mortar 1:3 over existing cement concrete bed ,including cost of materials, labour, curing complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin,etc. | 65 | sqm | 4372 | #NAME? | 284180
3.8 | Providing and fixing skirting of 300mm high using prepolished water cut/gang saw of 19mm thick grey granite 0.5mm wide chamfered width and depth and fixing in CM 1:4 of 20mm thick after chipping the walls, etc., including cost of all materials, mortar,labour,curing,etc., complete as per specifications.
a) | Office and control rooms in chlorine house, security cabin,etc. | 51 | RM | 1312 | #NAME? | 66912
3.9 | Providing dado, rises of steps with colour glazed tiles on 10mm thick cement plaster 1:3 and jointed with white cement slurry over rough plaster surface ( excluding cost of rough plastered surface which should be measured and paid separately) using glazed tiles of approved make and size including cost of materials, labour, complete as per specifications.
a) | chlorine house, reservoir staircase,etc. | 25 | sqm | 1299 | #NAME? | 32475
3.1 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tiles of approved make and colour of size 100 mm x 200 mm x 20 mm thick for flooring, on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Neutralization pit, walls and base slab | 110 | sqm | 4070 | #NAME? | 447700
3.11 | Providing and laying M-15 cement concrete flooring, 60mm thick with metallic concrete hardner topping, under layer of 45mm thick M-15 cement concrete using broken granite metal of 20mm and downsize and top layer of 15mm thick metallic cement hardner consisting of mix 1:2 by volume, with metallic hardening compound of approved quality mix in the ratio of 4:1, including finishing, cost of materials, labour, curing, complete as per specifications.
a) | Drum room and chlorinator room | 200 | sqm | 886 | #NAME? | 177200
3.12 | Providing and laying Ceramic Unglazed Vitreous Acid Resistant Tile dado of approved make and colour of size 100 mm x 200 mm x 20 mm thick for on a bedding and jointing of approved chemical resistant resin type of mortar, etc. complete as per specifications.
a) | Drum room and chlorinator room | 180 | sqm | 4070 | #NAME? | 732600
3.13 | Providing and fixing ceramic tiles (non skid) of size 400x400mm for flooring laid on a bed of 20mm thick cement mortar 1:3 mix flush pointing with white cement mixed with matching colour pigment including curing, cleaning,etc., complete.The work includes cost of all materials,mortar,labour charges for all items of work,hire charges for equipment,etc., complete as per specifications.
a) | Wash room of control and Office rooms | 100 | sqm | 1325 | #NAME? | 132500
3.14 | Providing, fabricating and fixing in position anodised aluminum doors using following aluminum sections mat or glossy finish, outer frame of section 101.6 x 44.45 x 3.18 mm at 2.404 Kg/m, door shutters vertical section - 44.62 x 44.45 x 3.00mm at 1.426 Kg/m, bottom section 114.3 x 44.45 x 3.18mm at 2.646 kg/m, top section 47.62 x 44.45 x 3.00mm at 1.426 kg/m, middle section 49.91 x 44.45 x 3.00mm at 1.495 Kg/m, glazing clips 19 x 17.3x 11mm x 0.90 mm thick at 0.124 kg/m, all sections anodised to 12 to 15 microns. Cut to length, joint mitred corners grinded, shutters pivoted opening arrangement with h eavy duty aluminum alloy automatic door closer, floor mounted, providing and fixing standard approved accessories such as aluminum handle, for full width or length, tower bolts, lock pivots, PVC or rubber gaskets with 5.5 mm thick plain glass for top and bottom panel, aluminum sections treated for removal of rust, coated with greasy material for non adherence of mortar or any sticky material, the assembled frame fitted with corner angles, strips and fitted with rawl plugs, or teak wood gutties, to RCC columns, or masonry sides, including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. as per specifications | 20 | sqm | 9472 | #NAME? | 189440
3.15 | Providing, fabricating and fixing in position Stainless steel doors including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. | 4 | sqm | 36429 | #NAME? | 145716
3.16 | Providing and fixing mechanical gear type rolling shutters of approved make out of 18 guage, 75mm wide cold rolled steel laths of convex corrugation, with side guides and bottom rail, with interlocking arrangements for steel laths by means of alternate clips, suspension shaft with High tension coil type springs two numbers, mounted on specially designed pipe shaft, with bracket plates, guide channels, ball bearing arrangements, for inside & outside locking complete including pulling hooks, 4Nos. handles with all fittings and accessories, painted with a coat of red lead paint (without top cover) cost of materials, labour, HOM of machinery complete as per specifications. | 21 | sqm | 7286 | #NAME? | 153006
3.17 | Providing and fixing hydraulic door closures -Aluminium body | 5 | Nos. | 2915 | #NAME? | 14575
3.18 | Providing and fixing mortice door lock heavy duty to doors. | 9 | Nos. | 2186 | #NAME? | 19674
3.19 | Providing and fixing in position anodized aluminium windows and ventilators as per approved drawings with sliding shutters using double track window frame section of size 61.85x31.75mm. with 1.2mm thick, bottom section weight 0.695 kg/m, sides and top sections 1.3 mm. thick weight 0.659 kg/m; and shutter comprising top and bottom section of size 40mmx18mm, 1.25mm thick 0.417 kg./m; shutter outer side 40mmx18mm, 1.25mm.thick weight 0.417 kg/m, shutter interlock section 40mmx26.7mm, 1.1mm thick, weight 0.469 kg/m. the shutters mounted on nylon rollers with approved quality of fixtures such as aluminium handles tower bolts etc.; and providing and fixing 5.5mm. thick plain glass for shutters fitted with rubber beading aluminium sections anodised 12 to 15 microns, including cutting to required length, joints mitred subdividing the frame tenonned and rivetted in the assembled frame stiffened with end clips at corners angles etc., and fixed to the walls, lintels, floor beams/cills as the case may be with necessary steel screws, raul plugs, or teak wood gatties including cutting masonry or concrete and making good the original surface using cement mortar, aluminium sections pretreated for removal of any rust and protection of further rust formation and coated with the greasy materials for non- adhesion of mortar and any other sticky materials, (this coating should be cleaned after installation) including cost of all materials, fixtures, labour and HOM of machinery complete as per specifications. | 50 | sqm | 7286 | #NAME? | 364300
3.2 | Providing, fabricating, assembling and fixing in position aluminium partitions with aluminium section anodized to 12-15 microns using sections in combination of plain, single grove and double grove as per requirements for the frames of overall size 101.6mm x 44.45mm, 3.18mm.thick having section weight, plain sections 2.40kg/m single grove section 2.541kg/m. and double grovesection 2.683 kg/m and bottom 46 kg/m; aluminium louvres of size 77.6mmx27.6mm 1.7mm. thick section weight 0.483kg/m; bottom portions provided with 12mm. thick prelaminated sheet both side of approved colour lamination exterior grade; aluminium sections of mat finish or glossy finish using section, spacing of vertical member shall not exceed 0.6 m. c to c; sections are cut to the required lengths, joints mitered and corners grinded subdividing frames tennoned and rivetted to the frames, the assembled frame should be stiffened with corner angles stripped and fixed with screws, rawl plugs and teak wood gutties to R.C.C.columns or masonry on sides, R.C.C. lintels or beams at top and floor at bottom, including cutting chistling and making good with cement mortar to match the surface, providing and fixing bottom panel filled with the materials to a height of 0.9m. from floor level; and 5.5mm. thick plain glass for middle portion viz., 0.9m. to 2.13 m. and top panel with lower sections, the glass and panels fitted with glazing clips of 19mmx17.3mm. with thickness of 0.9mm. weight 0.124kg/m; aluminium sections pre-treated for removal of any rust and prevention of further rust formation, and coated with greasy materials for non-adherence of mortars or any other sticky materials; vertical members embedded in the flooring by making suitable size holes and fixing with cement mortar, with necessary opening for fixing of doors of standard size including cost of materials, fixtures, labour and HOM of machinery complete. | 17 | sqm | 9472 | #NAME? | 161024
3.21 | Providing and fixing 225 mm wide and minimum 6 mm thick continuous PVC waterstops of approved quality at contraction and expansion joints as per manufacturer's instructions at all levels for Ground level reservoir. | 4997 | RM | 365 | #NAME? | 1823905
3.22 | Supplying and fixing PVC encapsulated CI rungs to shapes and at locations specified in drawings and specifications for Valve chambers | 228 | kg | 108 | #NAME? | 24624
3.23 | Providing and fixing 10 gauge aluminium sheet to required shape and size with rawl plugs and screws to concrete curbs to cover up expansion joints at roof level, including filling the notch with bitumen as specified in drawing, for Ground level reservoir. | 120 | sqm | 2264 | #NAME? | 271680
3.24 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant Type A) in a groove of size 15 mm x 20 mm deep at contraction joints including forming groove as specified on drawing for Ground level reservoir. | 3100 | RM | 387 | #NAME? | 1199700
3.25 | Providing and filling polysulphide rubberised sealing compound or equivalent (Sealant type B) in a groove of size 25 mm x 20 mm deep at expansion joints including forming groove as specified on drawing for Ground level reservoir. | 600 | RM | 401 | #NAME? | 240600
3.26 | Providing and fixing in position 25 mm thick sellotex board/filler compound as per standards and approved by the Engineer, of required sizes at expansion joints as specified in drawing for Ground level reservoir. | 250 | sqm | 328 | #NAME? | 82000
3.27 | Providing and laying 500 gauge polyethylene sheet of approved make and quality on blinding layer and wherever specified as directed by Engineer, for Ground level reservoir. | 13262 | sqm | 62 | #NAME? | 822244
3.28 | Providing and fixing slip-strip (1 mm thick PVC sheet) of approved quality or equivalent at junction between top of wall and bottom of roof slab in two layers as directed by Engineer, for Ground level reservoir. | 163 | sqm | 729 | #NAME? | 118827
3.29 | Providing and laying in position yelahanka tiles of size 125 x 250mm of approved quality and make, over a bed of cement mortar 1:3 with thickness varying from 100mm to 25mm including weather proof course and pointed with cement mortar 1:3 mix with red oxide including curing cost of materials, labour complete as per specifications. | 11942 | sqm | 1403 | #NAME? | 16754626
3.3 | Providing and fixing 150 mm diameter cast iron air ventilators as per design & shape indicated in drawings over roof slab of all reservoirs with mosquito proof jali etc complete. | 150 | Nos. | 6896 | #NAME? | 1034400
3.31 | Installing precast circular hume pipe septic tank suitable for 5 persons capacity conforming to IS 2470, and constructing standard soak pit for the same capacity, including excavation and backfilling of pit, PVC Pipe, filling soakpit with broken bricks, overflow connection precast RC slab and construction of manhole chamber with cover, C.I. vent pipe with cowl and connecting it to incoming and outgoing pipelines etc., complete. | 1 | Nos. | 145713 | #NAME? | 145713
3.32 | Supplying of and application of food grade epoxy painting on the inside surface of GLR headroom, GLR inside staircase and wall face at staircase complete, as per applicable Technical specification clause, including all labour, HOM of equipment, lead, lifts taxes etc., complete, including all surface preparation, testing, Rate shall be inclusive of all materials, tools and plants, testing and inspection etc., complete. | 100 | sqm | 481 | #NAME? | 48100
3.33 | Providing and laying M15 grade plain concrete in screed for required level above base slab of reservoir to specified slope with coarse aggregate of size 10mm downgraded including formwork and compacting with a hand rammer,curing,finishing,etc., complete as per specifications. | 3307 | Cum | 6871 | #NAME? | 22722397
3.34 | Providing and laying plain cement concrete of design mix M15 with OPC minimum cement content at 240kgs using 40 mm and down size graded granite metal course aggregates and the fine agregates machine mixed, concrete laid in layers with thickness varying from 150mm to 75mm over 230 mm thick rubble packing with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, etc., complete for plinth protection 1m wide as per drawings, details and specifications. | 90 | RM | 1689 | #NAME? | 152010
| TOTAL CARRIED TO BILL IIID SUMMARY |  |  |  |  | 52228420
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - IVD : WATER SUPPLY AND SANITARY WORKS
4.1 | Providing and fixing white vitreous china clay, water closet European type (Pedestal type, P-trap) with black solid plastic seat and lid, CP brass hinges, rubber buffers, 10 litre low level, P.V.C flushing cistern (all are approved make) with fittings, SS brackets, 40mm diameter flush bend with fittings and clamps, overflow arrangements with specials and 25mm mosquito proof coupling of approved design, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 14572 | #NAME? | 29144
4.2 | Providing and fixing white vitreous china clay, flat back wash basins of size 550 mm x 400 mm with a pair of 15mm C.P brass pillar taps with SS brackets, 32mm C.P brass waste of standard pattern, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 8743 | #NAME? | 17486
4.3 | Providing and fixing white vitreous china clay, flat back, lipped front urinal basin of 430x260x350mm in the range of three with 7.5 litres PVC automatic flushing cistern, SS brackets, standard flush pipe and C.P brass spreaders with brass unions and G.I clamps painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 7286 | #NAME? | 14572
4.4 | Providing and fixing in position brass bib cock of aproved quality 15mm nominal bore including cost of all materials, labour and HOM of equipments with all leads complete as per specifications. | 3 | Nos. | 1458 | #NAME? | 4374
4.5 | Providing brick masonry inspection chambers, rectangular in size 90 cm x 45 cm and upto 1.5 m depth on sewer line , with 230 mm brick wall in cement mortar (1:2), plastered both inside and outside with 20 mm thick cement mortar (1:2),including 1.6 m x 1.2 m x 290 mm thick cement concrete 1:2:4 in haunches as per standard plan including excavation, backfilling the excavated sides and removing surplus earth and with heavy duty C.I. cover and frame and with M.S. steps fixed in cement mortar with cement and sand filleting. | 2 | Nos. | 26223 | #NAME? | 52446
4.6 | Same as in for item 4.5 above but for depth greater than 1.5 m and upto 3 m | 2 | Nos. | 38907 | #NAME? | 77814
4.7 | Constructing circular type manhole 1500mm internal dia at bottom, 525mm dia at top, in wire cut burnt brick masonry with 1:5 cement mortar, cement plaster 1:3, finish with a floating coat of neat cement, RCC 1:2:4 top slab using 20mm and downsize granite metal, foundation concrete, M7.5 using 40mm and downsize granite metal and making channels in cement concrete M15 using 20mm and downsize granite metal, neatly finished curing, fixing CI cover complete including external, footrests and 12mm thick cement plaster on the external surface, cost of materials, labour charges, HOM of machineries complete as per specifications. | 2 | Nos. | 75964 | #NAME? | 151928
4.8 | Providing and fixing PVC Nahani trap of approved make conforming to ISI specifications and construction of cistern in M-15 as per directions. (rate inclusive of cost of materials and fixtures and conveyance of materials to work spot). | 3 | Nos. | 875 | #NAME? | 2625
4.9 | Providing stoneware gully trap of approved quality and make fixing in M-15 and plastering with CM 1:3 wherever necessary. (rate includes cost of all materials, fixtures and lead). With 100mm outlet. | 2 | Nos. | 1458 | #NAME? | 2916
4.1 | Providing and fixing 75 mm dia PVC slotted vent cowls conforming to IS 3989 with necessary fixtures and as directed by Engineer. | 2 | Nos. | 729 | #NAME? | 1458
4.11 | Providing and fixing white glazed 'P' trap as per IS 2556 (Part 7) 100 mm dia with SS grating 10 mm thick etc., complete. | 1 | Nos. | 1458 | #NAME? | 1458
4.12 | Providing and fixing cast copper alloy stop valves, polished bright, conforming to and as per IS 781.
a) | 25 mm dia. | 1 | Nos. | 729 | #NAME? | 729
b) | 20 mm dia. | 2 | Nos. | 729 | #NAME? | 1458
c) | 15 mm dia. | 1 | Nos. | 729 | #NAME? | 729
4.13 | Providing and fixing SS towel rail 740mm length, 20mm dia with C.P brackets, fixed to wooden cleats with C.P brass screws including cost of materials, labour complete as per specifications. | 4 | Nos. | 2186 | #NAME? | 8744
4.14 | Providing and fixing best quality SS liquid soap bottle holders of approved make with SS brackets, screws, rawl plugs, etc. complete. | 3 | Nos. | 1458 | #NAME? | 4374
4.15 | Providing and fixing 600x450 bevellead edge mirror of superior glass with 6mm hard board backing and fixed to wooden cleats with C.P screws, washers, including cost of materials, labour complete as per specifications. | 4 | Nos. | 7286 | #NAME? | 29144
4.16 | Providing and fixing white glazed partition walls of size 825 mm x 450 mm x 25 mm as per IS 2556 (Part 6 ) of approved make, properly supported with C.I. brackets, etc. complete. | 2 | Nos. | 2911 | #NAME? | 5822
4.17 | Providing and fixing UPVC water pipes and fittings 'B' class pressure rating of 10kg/cm2 conforming to IS 13592 and IS14735, with all necessary fixtures and bends, including testing the line as specified,etc.,complete.
a) | 25 mm dia. | 100 | RM | 292 | #NAME? | 29200
b) | 20 mm dia. | 25 | RM | 219 | #NAME? | 5475
c) | 15 mm dia. | 10 | RM | 146 | #NAME? | 1460
4.18 | Providing and Fixing PVC soil waste and vent pipes 100 mm diameter - 10kg/cm2 with spun yarn soaked in cement slurry and cement mortar 1:2 including cost of materials, labour, testing complete as per specifications. | 200 | RM | 875 | #NAME? | 175000
4.19 | Providing and fixing PVC pipes of approved make and 150 mm dia - 10kg/cm2 conforming to IS 651, including all necessary fixtures and bends, including excavation, backfilling, testing etc., complete as per specification. | 200 | RM | 1284 | #NAME? | 256800
4.2 | Providing and fixing 100 mm dia - 10kg/cm2 PVC rain water pipes as per IS: 4984 including all fixtures such as brackets, bends etc.as directed by the Engineer. | 765 | RM | 315 | #NAME? | 240975
4.21 | Providing and fixing cast iron bell mouth rain water outlets including MS grating, etc., complete as directed by Engineer.
a) | 100mm Dia. | 90 | Nos. | 1458 | #NAME? | 131220
4.22 | Providing, supplying and fixing rectangular SS manhole covers with chains connecting to the frame of size 1200x900 and 900mm x 600mm of grade 304L for roof slab of reservoir and underground chambers at locations shown in drawing including SS frame etc. complete. | 850 | kg | 583 | #NAME? | 495550
4.23 | Supplying PVC pipes conforming to IS 4985:2000 with latest amendments and conveying to worksite, rolling and lowering into trenches, laying true to line and level and perfect linking at joints, testing and commissioning, including loading and unloading at both destinations and cuts of pipes wherever necessary including jointing of PVC and specials with jointing of approved type, with all labour with all lead & lifting. (75mm dia - 10kg/cm2) | 65 | RM | 729 | #NAME? | 47385
| TOTAL CARRIED TO BILL IVD SUMMARY |  |  |  |  | 1790286
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - VD : STRUCTURAL STEELWORKS
5.1 | Supplying, fabricating, delivering to site, loading, unloading, etc. and erecting structural steel work for the following works, including one shop coat of red oxide zinc chromate primer after fabrication and one coat of the same after erection and two coats of synthetic enamel paint of approved shade, etc. complete as per specifications.
a) | Chlorine house | 930 | kg | 108 | #NAME? | 100440
5.2 | Providing and fixing in position MS ladders as per drawing, including painting etc. complete. | 350 | kg | 117 | #NAME? | 40950
5.3 | Providing and fixing 304- grade Stainless steel handrails of 14 gauge pipe for ramps or staircase are made out of stainless steel hollow pipes, using 50mm dia for verticals @ 1.60mtr c/c are fixed to the rams or steps by drilling with bolts and 100mm dia MS base plates 10mm gauge for fixing of vertical pipes 4 nos anchor bolts & 40mm dia pipes are fixed horizontally for 2 rows top one pipe are fixed with vertical pipes another one are fixed with elbows & 25mm dia pipes are fixed horizontally for 2 rows with elbow top measure @ equal intervals including cutting, welding, bending wherever necessary with suitable caps @ tops, bottoms, corners finishing with mat/shining etc., completeincluding cost and conveyance of all materials, labour for all items of work, HOM of euipment with all lead and lift, loading and unloading, transportation charges and all other incidental charges etc., complete as per specification and directions of the Engineer-in-charge of the work. Ramps or staircase for physically challenged. | 630 | RM | 2889 | #NAME? | 1820070
5.4 | Providing and fixing MS frame with 10 mm thick flats with grating cover with stiffeners for openings as specified in drawing at all locations and levels, including painting, etc., complete. | 3500 | kg | 108 | #NAME? | 378000
| TOTAL CARRIED TO BILL VD SUMMARY |  |  |  |  | 2339460
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - VID : ROADWORKS
ROADS & DRAINS
6.1 | Construction of Granular sub-base for 200 mm by providing coarse graded material , spreading in uniform layers on prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density, complete as per clause 401 for Grading-v of MORTH V Specifications. | 570 | Cum | 2851 | #NAME? | 1625070
6.2 | Providing, laying, spreading and compacting 150 mm graded stone aggregate to Wet Mix Macadam (WMM) specification including premixing the material with water at OMC in mechanical mix plant carriage of mixed material by tipper to site, laying in uniform layers in sub base/ base course on well prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density. MORTH clause 406 | 342 | Cum | 3078 | #NAME? | 1052676
6.3 | Providing and applying Primer Coat with bitumen emulsion using emulsion pressure distributor at the rate of 0.60 kg per sqm on the prepared WMM surface including cleaning of WMM surface and spraying primer using mechanical spray jet as per MORTH V specification clause No. 502 complete in all respects. | 2280 | sqm | 34 | #NAME? | 77520
6.4 | Providing and applying Tack Coat on the prepared WMM surface hot bitumen primed at 1Kg per Sqm heating bitumen in boiler fitted with spray set as per MORTH V specification clause No. 503 complete in all respect. | 2280 | sqm | 57 | #NAME? | 129960
6.5 | Providing and laying Bituminous Macadam 50 mm thick from 100-120TPH hot mix plant using crushed aggregates of specified grading premixed with bituminous binder, transported to site, laid over a previously prepared surface to the required grade, level and alignment and rolled by virbratory roller as per MORTH V specification clauses 505 to achieve the desired compaction complete with all lead and lift and direction of Engineer-in-charge. | 143 | Cum | 10448 | #NAME? | 1494064
6.6 | Providing and applying Tack Coat on the prepared BM surface at 0.5Kg / Sqm heating bitumen in boiler fitted with spray set as per specification clause No. 503 of MORTH V complete in all respects. | 2850 | sqm | 28 | #NAME? | 79800
6.7 | Providing and laying Semi Dense Bituminous Concrete(SDBM) 25 mm thick with 100-120 TPH hot mix plant using crushed aggregates of specified grading, premixed with bituminous binder 5.4 to 5.6 per cent of mix and filler, transporting the hot mix to work site, laying with a hydrostatic paver finisher with mechanical control to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction as per MORTH specification clause No. 508 complete with all lead and lift, with 60/70 Grade bitumen and direction of Engineer-in-charge. | 71 | Cum | 11361 | #NAME? | 806631
6.8 | Construction of coverd drain 0.3m x 0.45m (inside dimensions) with RCC M20 grade 10cm thick for walls and floor, laid over 10cm thick 1:3:6 PCC bed and covered with M30 grade RCC slab 0f 15cm thick excluding earth work including reinforcement @ 35 kg/rmt and form work complete as per specifications. | 1140 | RM | 5724 | #NAME? | 6525360
COMPOUND WALL
6.9 | Earthwork excavation for foundation in all types of soil excluding hard rock including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50 m and disposal of excess excavated earth including all leads and lifts after breaking of clods complete as per specifications.
a) | 0 -1.5m | 2583 | Cum | 152 | #NAME? | 392616
6.10 | Providing and laying in position plain cement concrete of mix M10 with OPC cement @220kgs, with 20mm and down size graded granite metal coarse aggregates @ 0.84cum and fine aggregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms thick, well compacted, in foundation and plinth including cost of all materials, labour, HOM of machinery curing complete as per specifications. | 88 | Cum | 6409 | #NAME? | 563992
6.11 | Filling available excavated earth (excluding rock) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts including cost of labour complete as per specifications. | 879 | Cum | 73 | #NAME? | 64167
6.12 | Providing and laying in position Reinforced Cement Concrete of Grade M25 (Design mix) with 20mm and downsize graded granite metal machine mixed, concrete laid in layers not exceeding 15 cm thick, vibrated for R.C.C. beams, columns of all sizes in foundation, plinth and superstructure ground floor levels of roof slabs, base slab, staircases, lintels, columns including cost of all materials, labour, HOM of machinary, curing, complete as per specifications. | 312 | Cum | 7617 | #NAME? | 2376504
6.13 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for foundation, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specifications | 3500 | sqm | 729 | #NAME? | 2551500
6.14 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per speciications. | 1550 | sqm | 729 | #NAME? | 1129950
6.15 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications | 105 | sqm | 729 | #NAME? | 76545
6.16 | Providing TMT Steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, tying with binding wire and anchoring to the adjoining members whenever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinary complete as per specifications. (Fe 500 grade confirm to IS 1786). | 42 | MT | 69122 | #NAME? | 2903124
6.17 | Providing barbed fixed 12x12 guage drawn into stone pillar or iron pillars including drawing in holes wherever necessary excluding the cost of pillar but including the cost of barbed wire and binding wire etc., complete | 746 | RM | 132 | #NAME? | 98472
6.18 | M.S Angle | 532 | kg | 108 | #NAME? | 57456
6.19 | Providing and finishing external walls in two coats with waterproof paint with primer of approved brand and shade to give an even shade after thoroughly brooming the surface to remove all dirt and loose powdered material free from mortar drops and other foreign matter cost of materials, labour complete as per specifications | 3800 | sqm | 175 | #NAME? | 665000
6.20 | Supplying and fixing M.S rectangular poles made out of 2 equal angles of 65x65x6 mm welded together and fixed in CC (1:2:4) with 2 nos 16mm dia MS hold fast rods each of length 25cms including cost of all materials cutting,bending,scaffolding wherever necessary,nicely finishing the welded joints with all lead lifts and as per specifications including providing 2 coats of approved quality paint over one coat of shop painting. | 1200 | RM | 1337 | #NAME? | 1604400
6.21 | Providing chain link fencing 50mm size of 8 guage properly stretched between rectangular poles and fixed with suitable bolts & nuts, the free ends shall be welded to the pole and block pipe at top and bottom as required including cost of all materials, labour, lead and lifts and as per the directions of the Engineer in-charge of work including two coats of approved quality paint over one coat of shop paint. | 800 | sqm | 365 | #NAME? | 292000
6.22 | Providing and fixing MS block pipe of 38mm dia of heavy guage of 14 including removing the bends, cutting the pipe, and fixing pipe in between the two vertical poles (MS rectangular poles) and spot welding the chain linkwith MS block pipe including cost of all materials wastage in cutting, scaffolding wherever necessary with all lead and lift,etc., complete including two coats of approved quality paint over one coat of shop paint. | 500 | RM | 209 | #NAME? | 104500
6.23 | Providing and erecting in position., 2400x600x60 mm thk precast slab panels of M25 grade reinforced cement concrete including reinforcement and formwork with coarse aggregate of size 20mm downgraded with minimum cement content of 320kg/cum. The reinforcement consists of 1 no of 10mm dia loop and round the panel, 5 nos of 8mm dia horizontals and 15 nos of 8mm dia verticals equally spaced. The thickness of the panel shall be 60mm thick at the middle and 70mm thick at the edges for a width of 250mm.The gaps between the panels shall be packed with 1:4 cement mortar and the final surface between the panel and RCC post shall be finished using silicon sealant of approved make, complete as per specification & drawing.
a) | For both side plain finished panels of 2400mm x 600mm size, as shown in the drawings. | 304 | Nos. | 3524 | #NAME? | 1071296
b) | For one side plain and other side with horizontal grooves as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 304 | Nos. | 3524 | #NAME? | 1071296
c) | For one side plain and other side with vertical grooves as as per the design pattern panels of 2400mm x 600mm size, as shown in the drawings. | 304 | Nos. | 3524 | #NAME? | 1071296
d) | For one side plain and other side with BWSSB logo as per the pattern panels of 2400mm x 600mm size, as shown in the drawings. | 304 | Nos. | 3524 | #NAME? | 1071296
6.24 | Providing and fixing gates consisting of 40 mm NB light glass GI pipes external framework and 8 x 30 MS flats internal framework with 16 guage MS jointing plates and tack welded over the framework with necessary hinges and locking arrangement, including painting over approved primer coat, etc. all complete as per specifications and drawings. | 2 | MT | 107603 | #NAME? | 215206
| TOTAL CARRIED TO BILL VID SUMMARY |  |  |  |  | 29171697
Part 2D : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - VIID : PIPEWORKS, VALVES AND SPECIALS
Pipelines, Specials and Appurtenances
7.1 | Providing, Fabricating, shop welding, transporting, handling, aligning, laying and jointing / welding of MS pipes of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate also include loading and unloading, radiography of joints as specified and hydraulic testing of pipeline to specified pressure as per specifications and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings.
a) | 1500 mm internal diameter with 10 mm shell thickness Overflow Pipe of GLR | 5 | RM | 29058 | #NAME? | 145290
b) | 1400 mm internal diameter with 9 mm shell thickness Inlet and outlet pipe of GLR | 5 | RM | 24403 | #NAME? | 122015
7.2 | Providing, fabricating, shop welding, handling, transporting, aligning, laying and jointing of MS specials of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate include loading and unloading, radiography of joints as specified and hydraulic testing of specials to specified pressure and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings. | 3500 | kg | 139 | #NAME? | 486500
7.3 | Providing guniting (CM 1:3 over 50 x 50 mm weld mesh of 13 gauge) on the external surface of pipes and specials including supplying and fixing reinforcement as per specifications after cleaning the pipes including curing etc., at fabrication yard and guniting the field joints at site between two pipes after testing complete in all respects as per specifications.
a) | 1521 mm OD pipes and specials, 25 mm thick guniting | 25 | Sq.m | 729 | #NAME? | 18225
b) | 1419 mm OD pipes and specials, 25 mm thick guniting | 23 | Sq.m | 729 | #NAME? | 16767
7.4 | Providing food grade internal epoxy lining of 0.5 mm thick as per specifications to the internal surfaces of mild steel pipeline, fittings, specials etc., including surface preparation, machine lining, curing and testing / inspection etc., complete.
a) | 1500 mm ID pipes & specials to 1500 mm finished diameter, 0.5 mm thick internal epoxy lining | 23 | Sq.m | 583 | #NAME? | 13409
b) | 1400 mm ID pipes & specials to 1400 mm finished diameter, 0.5 mm thick internal epoxy lining | 21 | Sq.m | 583 | #NAME? | 12243
7.5 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Motorised operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 1400 mm dia PN 16 for 1400 mm ID | 4 | No. | 2275629 | #NAME? | 9102516
7.6 | Supply,installation, testing & Commissioning of (Scour purpose) Ductile Iron (DI) Resilient seated soft sealing sluice valve. Detailed Valve specifications & arrangement shall be as defined in Volume 2. The rate is inclusive of cost of mating flanges, valve,bolts & nuts and rubber insertions,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 300 mm dia. PN 16 size scour valves for GLR | 2 | No. | 55047 | #NAME? | 110094
7.7 | Providing, supplying and fixing SS 304 Expansion Bellows with Flange Ends as per specifications and drawings.Detailed Specifications & arrangement shall be as defined in Volume 2. The rate shall include transportation to site with all leads and lifts, aligning and jointing approved anti-corrosive paint etc., complete in all aspects. Rates are incluisve of Labour Charges.
a) | 1400 mm dia. PN 16 | 6 | No. | 371785 | #NAME? | 2230710
7.8 | Providing and laying following dia of MS pipes conforming to IS 3589 in trenches outside the pipeline scour valve chambers for draining, include lining & coating, excavation, connecting to scour valve, backfilling the earth etc., complete.
a) | 300 mm dia. 5.6 mm thick | 60 | RM | 3294 | #NAME? | 197640
| TOTAL CARRIED TO BILL VIID SUMMARY |  |  |  |  | 12455409
Part 2D : MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - VIIID : MECHANICAL WORKS
8.1 | Mechanical Equipment
a) | Supply,Testing, Installation & Commissioing of 11 Kg/hr Capacity with 0-2 ppm dosage level Vaccum type Chlorination System 2 sets.(1W+1S) with all allied works complete as per Bid specification of Volume 2
(i) | 11 Kg/hr | 2 | Sets. | 1635618 | #NAME? | 3271236
b) | Supplying,Testing, Installation & Commissioing of Chlorine gas Filled Chlorine Tonners of 900 Kgs with all allied works complete as per Bid specification of Volume 2 | 4 | Nos. | 189426 | #NAME? | 757704
c) | Supply,Testing, Installation & Commissioing of Electrically operated wire rope hoist of 2 Ton capacity conforming to IS 3938 for chlorine house with suitable I-Beam arrangement and Electrical Panels etc.with all allied works complete as per Bid specification of Volume 2 | 1 | Nos. | 291461 | #NAME? | 291461
d) | Service Water Network system
(i) | Providing, erecting and giving test of Centrifugal Monoblock Pump set conforming to IS 9079 operating at 1500 RPM with pump casing: Cast Iron IS 210 FG Gr.260, Impeller:Bronze IS 318 LTB2, Shaft:SS 410 , Pump Seal: Mechanical Seal, priming funnel, cock, suitable flanges at suction and delivery side. Pump shall have common shaft for pump and motor. Motor shall be suitable for working on 2.0 HP, 415 V + 10%, 3 Ph, 50Hz+/-5% A.C. Supply. Motor shall be TEFC type. Pump set shall be suitable for working at various discharge and head requirements. Pump shall be erected on Provided C.C. foundation block with suitable foundation bolts grouted in C.C foundation block. | 2 | Nos. | 56935 | #NAME? | 113870
(ii) | Pressure Gauge: Supply, delivery at site and fixing of glycerine filled stainless steel pressure gauge of 100 mm Dia. suitable for the above pump sets with nipple, stop cock and three way cock for cleaning and necessary length of SS tubing suitable for mounting on the suction and delivery of pump, including 15 NB isolating valve etc., complete with all lead and lifts etc, complete as per specification | 2 | Nos. | 1909 | #NAME? | 3818
(iii) | Providing and fixing in position brass gate valve with CI wheel (screwed end) 40 mm nominal bore including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 6 | Nos. | 8109 | #NAME? | 48654
(iv) | Providing and fixing in position 40 mm nominal bore non-return valve vertical type of approved make including cost of all materials,labour and HOM of equipments with all leads complete as per specifications. | 2 | Nos. | 8960 | #NAME? | 17920
(v) | Providing & Fixing to wall,ceiling and floor high density polyethylene pipes 6.00 Kgf/sq.cm working pressure of outside diameter raising mains & exposed distribution pipes with special flange, compression type fittings, wall clips, making good the wall, ceiling and floor, including cost of all materials, labour charges, HOM and testing complete as per specifications.
i | 40 mm dia | 100 | RM | 219 | #NAME? | 21900
(vi) | Providing and placing on terrace,polyethylene water storage tanks with manhole lid and suitable locking arrangements,making holes of suitable diameter for inlet,outlet and overflow pipes,including cost of all materials,labour transportation charges,HOM of equipments and testing complete as per specifications (for 1000 litres capacity) within the GLR Campus. | 1 | Nos. | 14572 | #NAME? | 14572
| TOTAL CARRIED TO BILL VIIID SUMMARY |  |  |  |  | 4541135
Part 2D : INSTRUMENTATION WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - IXD : INSTRUMENTATION WORKS
9.1 | ICA Items for City reserviors
a) | Designing, Supplying, Installing, commissioning & testing of Ultrasonic level transmitter with following technical parameters at GLR and Interfacing with PLC panel including all required Mounting accessories, factory testing & inspection complete as per specifications. Range : (0 - 10 m) | 2 | Nos. | 62344 | #NAME? | 124688
b) | Supply, delivery at site and fixing of Conductivity type Level Switch (back up to level transmitter), High Level & Low Level sensing - (4point contact) with necessary instrumentation cabling,glands with suitable stub and flange and bolting arrangement for hook-up, as applicable and necessary, factory testing & inspection. Range : (0 - 10 m) | 2 | Nos. | 78049 | #NAME? | 156098
c) | Design, Supply, Installation, Testing of Residual chlorine analyzer at GLR and Interfacing with PLC panel and factory testing for complete functional test & inspection. | 1 | Nos. | 227160 | #NAME? | 227160
9.2 | Instrument & power supply cables, supplies, laying, termination & testing.
a) | Plain annealed multistranded tinned copper conductors; solid polyethylene insulation with each pair screened with aluminium-mylar tape including drain wire, with collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (2 Pair x 1.5 sq.mm) | 200 | RM | 782 | #NAME? | 156400
b) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (12 Core x 1.5 sq.mm) | 200 | RM | 1434 | #NAME? | 286800
c) | Plain annealed multistranded tinned copper conductors, solid polyethylene insulation collective aluminium mylar tape screen including drain wire, solid polyethylene bedded steel wire armour with an outer sheath of flame retardant PVC. (4 Core x 1.5 sq.mm) | 300 | RM | 1141 | #NAME? | 342300
d) | Conduits and Supports (19mm OD Heavy Mechanical Stress PVC Conduit (Socketed) + Round Elbow + Circular Box (Through,Tee,Intersection,etc) + Coupler (Pipe to Pipe, End Cap) | 1 | Lot | 71627 | #NAME? | 71627
| TOTAL CARRIED TO BILL IXD SUMMARY |  |  |  |  | 1365073
Part 2D : ELECTRICAL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - XD: ELECTRICAL WORKS
LT Electrical Works for GLR Premises
10.1 | Supplying and erecting four pole metal clad ON LOAD change over switch 415V, 125A erected on angle iron /GI frame approved make complete. | 1 | No. | 10257 | #NAME? | 10257
10.2 | Supply, Transportation, loading/unloading, Laying, Installation & Commissioning of Solid Aluminum conductor up to 10 sqmm balance stranded conductor, XLPE Insulated, cores laid up, PVC tape/Extruded Innersheathed for Multicore Cables , Armour (Aluminium wire for single core up to 70 sqmm balance Aluminium strip, Glavanised wire for cables upto 2x10 sqmm, 3x10 sqmm,4x6 sqmm balance all galvanised steel strip), extruded PVC Type ST2 sheathed, 650/1100V grade as per IS 7098(Part 1) 1988, Incoming Cable from nearst 415V overhead line as per ESCOM specifications a) Metering Box to Change Over Switch b) Change Over Switch to 415V Panel Board
a) | 3.5C x 50sq.mm (Al. Conductor) | 70 | Mtr. | 263 | #NAME? | 18410
b) | 3.5C x 50sq.mm (Al. Conductor) - Glands | 4 | No. | 98 | #NAME? | 392
c) | 3.5C x 50sq.mm (Al. Conductor) - Lugs | 16 | No. | 50 | #NAME? | 800
10.3 | 415V PMCC Panel Board (Including Chlorine MCC): Supply, Transportation, Installation, Testing & Commissioning of 415V LT Board of cubicle type with 415V, 50 Hz, 3 PH, TPN, 25 kA for 1 sec, wtih IP-54 enclosure with Bottom entry, consisting of incoming and outgoing feeders with metering and protection with complete accessories as per specification and single line diagram.
a) | Incomer: 125A, 25kA, 4P, MCCB | 1 | No. | 10850 | #NAME? | 10850
b) | Outgoing: 25A TPN MPCB (Motorised Valves) | 5 | No. | 4307 | #NAME? | 21535
c) | Outgoing: 63A TPN MCCB (Indoor Lighting DB 1 & 2, Spare 2Nos.) | 4 | No. | 9074 | #NAME? | 36296
d) | Outgoing: 32A TPN MCCB (2T Crane, Spare 2Nos.) | 3 | No. | 7112 | #NAME? | 21336
e) | Supplying & erecting LED type indicating pilot lamp with LED colours red , yellow and blue, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 1 | Set | 1697 | #NAME? | 1697
f) | Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. | 34 | No. | 566 | #NAME? | 19244
g) | Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod upto 250A MCCB | 8 | No. | 1465 | #NAME? | 11720
h) | Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 100/5A, 5 VA , class 1 accuracy | 3 | No. | 625 | #NAME? | 1875
i) | Multi Functions Meters - Flush type for M V Panel Board LED type, CT/PT, Voltage, Current, Frequency, Kilowatt, Kilo Volt Ampere, KVAR , KVAH, Run Hours, unbalance(V,A),Rpm, Phase angles,Thd-Class 1 With RS 485 Port | 1 | No. | 10390 | #NAME? | 10390
j) | Supplying, erecting & marking SPMCB 5A in provided distribution board | 3 | No. | 571 | #NAME? | 1713
k) | DOL Feeder a) 25A MPCB - 1No b) Supplying and erecting D.O.L. Starter 400V. 3 phase, 50 cycles with no volt coil and overload element with necessary materials and connected to supply upto 7.5 H.P. - 1No. c)Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. d) Supplying, fixing and wiring 0 to 30amps Ammeter Analog SR 65 5D/5A C.T.operated-AC - 1No. e) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 30/5A, 5 VA , class 1 accuracy - 1No. | 8 | No. | 8943 | #NAME? | 71544
l) | Push button station / Local Control Panel near Pump a) Push Buttons (Start & Stop including emergency Stop). - 3Nos. b) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc - 3Nos. c) The cost for fabrication panel, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 8 | No. | 3010 | #NAME? | 24080
m) | Supply and fixing of Electrolytic grade copper bus bar bus bar by means of SMC / DMC type insulator, high tensile nuts and bolts spring washers in existing panel including bending , cutting in required shape and size and colour coding with heat shrinkable PVC sleeves | 28 | Kg | 987 | #NAME? | 27636
n) | 415V PMCC Panel Board Fabrication with enclosures, earthing bus, wiring, control relays, Auxiliary contactors, Control Transformers, power contactors, Control MCBs, terminal blocks etc. All complete works. | 1 | Set | 86961 | #NAME? | 86961
10.4 | Indoor Lighting DB: Supply, Transportation, Installation, testing & Commissioning of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos DP outgoings and for 1 No 4 pole Incomer with IP-54 enclosure, bottom entry cable, necessary accessories like wiring, contactors, terminal block, aux. relays, timer etc complete. a) Incomer: 63A, TPN, MCCB and 100mA, RCCB b) Outgoings: 6-32A, DP, MCB - 8 Nos and 32A TPN MCB - 3Nos c) Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod 63A MCCB - 1No. d) Supplying, erecting & marking SPMCB 5A in provided distribution board - 3Nos. e) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. - 6Nos. f) Supplying and erecting panel mounting type digital ammeter having three and half digit LED display, external CT operated, calibrated for suitable to operate on 500V, 0 to 1000A AC supply with necessary PVC wire leads and lugs and mounting hardware on provided panel complete with calibration certificate from manufacturer.. - 1No. g) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 60/5A, 5 VA , class 1 accuracy.- 3Nos. | 2 | No. | 41716 | #NAME? | 83432
a) | The cost for fabrication panel, Copper / Al busbars, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 2 | Set | 14601 | #NAME? | 29202
10.5 | Outdoor Lighting DB
a) | Supply of Way TPN DB Horizontal with IP 43 Protection suitable for 6DP out goings and for 1 No 4 pole Incommer etc complete as per IS 8623; IS 13032; IEC 61439-3. | 2 | No. | 1527 | #NAME? | 3054
b) | Supplying, erecting & marking DPMCB 16A B- series (for lighting) in provided distribution board | 8 | No. | 1068 | #NAME? | 8544
c) | Supplying, erecting & marking TPNMCB 32A in provided distribution board | 2 | No. | 2014 | #NAME? | 4028
10.6 | Lighting system (indoor and outdoor):
a) | Supply of Lighting Luminiares
i) | Supply, transportation and fixing of 36W Recessed / Surface mounting 2' x 2' (600x600 mm) LED luminaire made of CRCA sheet housing with powder coated with acrylic diffuser, Constant current Driver as per IS: 15885 (Part 2/ Sec 13) : 2012, With System lumen output ≥3200lm operating voltage range of 150 to 265 Volts AC, P.F > 0.9, Surge protection: 2KV, THD<10%, with high power LED's having efficacy of > 120 lumins / watt, CCT: 3000K - 5700K, minimum CRI>70, .etc.,, complete. | 30 | No. | 4761 | #NAME? | 142830
ii) | Emergency Lighting: Supply & Fixing of Rechargeable emergency lamp (600 mm fluorescent lamp) or LED lamp with accessories complete | 4 | No. | 2703 | #NAME? | 10812
b) | Fixing all types and all capacities of LED fittings on the wall / ceiling / rafters / girders using 23 / 0.0076” twin twisted PVC insulated wires, required Nos of round blocks and clamps. | 28 | No. | 216 | #NAME? | 6048
c) | Supply and transportation of LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 110 lm/W and junction temprature < 70°C, with Ingrees protection IP66, Luminaire performance complies to IS 10322 (Part 5 / Sec-3), Driver surge protection 4KV, external Surge protection 10 KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete
i) | 150W | 18 | No. | 11262 | #NAME? | 202716
ii) | 60W | 10 | No. | 5018 | #NAME? | 50180
d) | Supplying and erecting street light / Peripheral light bracket for erection of single fitting made from 40 mm. dia ‗B‘ class G.I. pipe 1.0 m in length along with pole cap of 300 mm length 100 mm dia duly welded | 10 | No. | 765 | #NAME? | 7650
e) | Fabrication, Transportation and supply of hot-dip galvanized Octogonal Pole with BSEN - 10025 grade S 355 JO steel plate for shaft, IS 2062 for base plate with door opening arrangement, including the supply of suitable boards with bakelite sheet as per IS specification suitable to withstand the wind speed of 180 KMPH for 7.5 Mtrs height Pole having dimensions Bottom 130 mm,. Top 70mm with 3mm thick, base plate 220 x 220 x 12mm and 4 Nos of M20 x 700 long 'J' bolts along with template. | 18 | No. | 11225 | #NAME? | 202050
f) | Fabrication, Transportation and supply of 1 / 1.50 Mtr Length Single Arm Bracket made with MS galvanized 40mm / 50mm dia Pipe. (Pole Brackets) | 18 | No. | 1934 | #NAME? | 34812
g) | Foundation and erection charges with special T&P, for 7.5 Mtrs long Octagonal duly erecting on base plate duly providing 4 Nos foundation bolts with nuts with providing of 0.45Mtr x 0.45Mtrs x1.20 Mtr size M20 cc work vibrated concreting mixing with necessary steel (10kgs) reinforcement and curing for 7 days as directed by the field engineers during execution including excavation of Earth/BT all labour charges and cost and conveyance of materials etc.complete. | 18 | No. | 8302 | #NAME? | 149436
h) | Supply of following sizes thermo plastic cable junctions boxes IP 65 protection with metric knockouts for cable entry including threaded cable gland. (260X210X116) | 18 | No. | 1557 | #NAME? | 28026
10.7 | Supply & Installation of Earthing system
a) | Providing earth electrode of low carbon steel rod, UL listed of 17.2 mm dia, 3 Mtr long, coated with copper of 254 microns thickness, CPRI tested for short time current withstand test of 25 kA, coating thickness, environmental test (Salt Mist Test), Bend test, Tensile strength, Yield / tensile ratio, Electrical Resistivity test, complete with clamps and 2 bags of Earthplus ULTRA high grade earthing compound IEC 62561-7 complaint Eco-friendly, Maintenance free, anti corrosive, lead-free, super conductive, mineral based high-grade earthing compound, to enhance soil conductivity. With resistance <0.20 ohmsmeter, should be leach proof & sulphur free complete with earth inspection chamber of dimensions : Width : 320 mm x 320 mm, Height : 192 mm, Weight : 30 Kgs, Load bearing capacity :5000 Kgs | 4 | No. | 9489 | #NAME? | 37956
b) | Supplying and running of GI strips & GI wire for grounding connections, using necessary fixing materials as required.
i) | 32x6 mm GI Earth Strip (For 415V PMCC & Outdoor Lighting Circuit) | 600 | Mtr. | 160 | #NAME? | 96000
ii) | 25x6 mm GI Earth Strip (for Lighting panel & LDB) | 200 | Mtr. | 116 | #NAME? | 23200
iii) | 8 SWG GI Wire (Junction box, Motorised valves etc.) | 250 | Mtr. | 19 | #NAME? | 4750
10.8 | Supply & Installation of Lightning Protection System
a) | Supply of Standard / Special Mounting Structure of height 4.5 mts. pipe, and 300 x 300 x 8mm MS plate, 3 mts. 48mm OD class C GI outer pipe,1.8 mtr, 38mm OD inner pipe, for roof mounting on concrete base and with FRP adapter | 1 | No. | 18777 | #NAME? | 18777
b) | Supply and run of 25mm x 6mm GI Flat Down Condutor with necessary clamps / supports on wall / floor / ground for earth connection | 300 | Mtr. | 116 | #NAME? | 34800
c) | Supply of Test Link Box for each Down conductor in order to disconnect the earth termination system to enable measurement of resistance | 1 | No. | 4620 | #NAME? | 4620
d) | Supply and insallation maintenance free Gl Earthing System comprising of 50mm dia and 2 mtr. long earth electrode of low carbon steel rod with 100 micron bonding and 25 kgs. of carbon based environment friendly backfill compound and suitable clamp | 1 | No. | 8530 | #NAME? | 8530
10.9 | Point Wiring for lighting/fan circuits & sockets
a) | Supply of ISI marked 40mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe | 120 | Mtr. | 88 | #NAME? | 10560
b) | Supplying and erecting unbreakable concealed type modular switch box with double mounting plate for 6 module duly erected flush to wall with required chiselling and finishing with cement mortar / POP as per required to match the background. | 12 | No. | 190 | #NAME? | 2280
d) | Supply of ISI marked 25mm / 32mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe.
i) | Short point (not exceeding 3m) | 40 | Mtr. | 77 | #NAME? | 3080
ii) | Medium point above 3m and up to 6m | 60 | Mtr. | 77 | #NAME? | 4620
iii) | Long point above 6m and up to 10m | 40 | Mtr. | 77 | #NAME? | 3080
e) | Supply of 4 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 80 | Mtr. | 38 | #NAME? | 3040
f) | Supply of 2.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 380 | Mtr. | 27 | #NAME? | 10260
g) | Supply of 1.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 170 | Mtr. | 18 | #NAME? | 3060
h) | Supply & Fixing of modular switch & connected accessories on existing switch plate and enclosure
i) | 32A TPN MCB + 40A TPN RCCB (socket-Industrial Type) | 2 | No. | 8305 | #NAME? | 16610
ii) | One/Two way piano type switch 6A | 20 | No. | 92 | #NAME? | 1840
iii) | 3 pin plug socket 6A | 15 | No. | 139 | #NAME? | 2085
iv) | Piano type switch 16A | 2 | No. | 213 | #NAME? | 426
v) | 3 pin plug socket 16A | 2 | No. | 152 | #NAME? | 304
i) | Supplying and erecting five star rated energy saving Ceiling fan 230 V A.C. 50 cycles 1200 mm complete erected in position | 2 | No. | 3091 | #NAME? | 6182
10.1 | Supply, Installation, Testing and commissioning of safety procedures for Electrical Equipments as per scope, specification and drawings.
a) | Supplying and Fixing PVC synthetic elastomer electrically insulating mat with class D insulation conforming to IS:15652-2006 and CPRI tested upto 11kV | 2 | No. | 6086 | #NAME? | 12172
b) | Supplying and Erecting Carbon Dioxide (CO2) fire extinguisher of 4.5 kg capacity cartridge type conform to IS 2876/15683 complete erected with necessary clamp made of 50x6 mm M.S. flat nut and bolts grouted in wall complete | 3 | No. | 11252 | #NAME? | 33756
c) | Supplying rubber gloves of 15KV conforming to IS for electrical purpose. | 2 | pairs | 1294 | #NAME? | 2588
d) | Supplying standard first aid box with necessary antiseptic cream, medicine for use on wounds due burn, crepe bandage, gauge bandage, medicated ready to use bandage (Band-Aid) adhesive tape for medicinal use, scissors, anti-septic solution, etc. (All above contents shall be of standard makes) | 1 | No. | 917 | #NAME? | 917
e) | Supplying and fixing of shock treatment chart on the wall with inside plastic sheet cover and plywood back plate frame work complete | 2 | No. | 774 | #NAME? | 1548
f) | Supplying and fixing of danger board made out of MS sheet metal with duly painted with red oxide and enamel paint. | 2 | No. | 129 | #NAME? | 258
g) | Tools and Plant
i) | Live Line Tester | 5 | No. | 92 | #NAME? | 460
ii) | Insulation Tester (Megger) 2.5kV-5kV | 1 | No. | 5911 | #NAME? | 5911
iii) | Multimeter electronic type | 2 | No. | 1183 | #NAME? | 2366
iv) | Earth Resistance Tester | 2 | No. | 7092 | #NAME? | 14184
v) | Rubber Shoes Knee Height | 3 | No. | 629 | #NAME? | 1887
vi) | DC Voltmeter range - 3V to +5V | 3 | No. | 591 | #NAME? | 1773
| TOTAL CARRIED TO BILL XD SUMMARY |  |  |  |  | 1713436
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - XID : MISCELLANEOUS WORKS
Pipelines, Specials and Appurtenances
11.1 | Providing, Fabricating, shop welding, transporting, handling, aligning, laying and jointing / welding of MS pipes of spirally welded/Plate welded pipes, conforming to IS 10748 Grade 3 for spirally welded/IS 2062 Grade B for Plate welded. The rate also include loading and unloading, radiography of joints as specified and hydraulic testing of pipeline to specified pressure as per specifications and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings.
a) | 1500 mm internal diameter with 10 mm shell thickness Overflow Pipe of GLR | 25 | RM | 29058 | #NAME? | 726450
b) | 1400 mm internal diameter with 9 mm shell thickness Inlet and outlet pipe of GLR | 50 | RM | 24403 | #NAME? | 1220150
11.2 | Providing guniting (CM 1:3 over 50 x 50 mm weld mesh of 13 gauge) on the external surface of pipes and specials including supplying and fixing reinforcement as per specifications after cleaning the pipes including curing etc., at fabrication yard and guniting the field joints at site between two pipes after testing complete in all respects as per specifications.
a) | 1521 mm OD pipes and specials, 25 mm thick guniting | 120 | sqm | 729 | #NAME? | 87480
b) | 1419 mm OD pipes and specials, 25 mm thick guniting | 224 | sqm | 729 | #NAME? | 163296
11.3 | Providing food grade internal epoxy lining of 0.5 mm thick as per specifications to the internal surfaces of mild steel pipeline, fittings, specials etc., including surface preparation, machine lining, curing and testing / inspection etc., complete.
a) | 1500 mm ID pipes & specials to 1500 mm finished diameter, 0.5 mm thick internal epoxy lining | 118 | sqm | 583 | #NAME? | 68794
b) | 1400 mm ID pipes & specials to 1400 mm finished diameter, 0.5 mm thick internal epoxy lining | 220 | sqm | 583 | #NAME? | 128260
11.4 | Supply,installation, testing & Commissioning of Ductile Iron (DI) Manually operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,Valve, bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges.
a) | 1400 mm dia PN 16 for 1400 mm ID | 2 | Nos. | 1842014 | #NAME? | 3684028
11.5 | ICA Items for City reserviors
a) | Supply, delivery at site and fixing of Electromagnetic Flow Indicating Transmitter (full bore type) with flange Ends, rates shall be inclusive of mating flanges with necessary fasteners and gaskets, as applicable and necessary.
(i) | Inlet of the reservoir, pipe size 1400 mm | 1 | Nos. | 1025494 | #NAME? | 1025494
11.6 | Miscellaneous Instruments
a) | Designing.supplying, Installing commissioning & testing of Surge Protection Devices | 6 | Nos. | 32558 | #NAME? | 195348
b) | Designing,supplying, Installing commissioning & testing of online UPS with AC Distribution Board(Min 5 KvA Industrial UPS with 60 min backup on full load of field instrumentation and control equipment inclusive of communication equipment to transfer data to CSC) and factory testing & inspection. | 1 | Nos. | 14650 | #NAME? | 14650
c) | supplying, Installing commissioning & testing of Junction Boxes | 4 | Nos. | 18279 | #NAME? | 73116
d) | supplying, Installing commissioning & testing of Field Instrument enclosures-IP 65 rated for all field instruments. | 7 | Nos. | 8954 | #NAME? | 62678
11.7 | Automation System
a) | Designing.supplying, Installing commissioning & testing of hot standby PLC with 16" colour HMI to control valves and to monitor the level and flow in the facility with required SCADA software.HMI shall be color with touchscreen functionality for complete auto operationm with FAT & SAT as per Contract requirements.(also include integration of flowmeter data (flowmeter’s which has been installed under other contracts) with the PLC based control system for continuous monitoring of both incoming and outgoing flow data at each location. All required cabling for connection, required hardware (splitters) with the PLC based control system shall be integral part of scope of work under this contract) | 1 | Nos. | 1074393 | #NAME? | 1074393
b) | Designing, supplying, installing, commissioning & testing of CCTV IR water proof camera suitable for upto 100ft.with IR Dome camera, control key board, DVR, Hard Disk, cables, UPT transreceivers etc. complete. (Close Circuit Television System to be installed at the reservoir locations to cover all areas of the facilities) and factory testing & SAT. | 4 | Nos. | 26866 | #NAME? | 107464
c) | Designing, supplying, testing & implementation of MIS Software for complete project as per specifications defined in Vol. 2 (From the start date to end End handing over) (Lingadernahalli,Singapura,Vasudevpura,Chhokanahalli) | 1 | Nos. | 1740472 | #NAME? | 1740472
d) | Implementation and Maintenace of MIS Software through out the construction period till end handing over as per specifications | 30 | Months | 39719 | #NAME? | 1191570
Electrical
11.8 | LT Cables
a) | Supplying, Erection & Termination of XLPE armoured cable copper conductor continuous 5.48 sq.mm. (12 SWG) GI earth wire complete erected with glands & lugs, on wall/trusses/pole or laid in provided trench/pipe as er PWD specifications.
(i) | 4C x 6 Sq.mm (LDBs, Recepacle, EOT Crane, etc.,) | 280 | Mtr. | 280 | #NAME? | 78400
(ii) | 4C x 4 Sq.mm (Street Lighting) | 620 | Mtr. | 209 | #NAME? | 129580
(iii) | 3C x 4 Sq.mm (Pumps, Valves motors, Lighting ckts, 1-ph sockets etc.,) | 1250 | Mtr. | 171 | #NAME? | 213750
(iv) | 3C x 2.5 Sq.mm (Outdoor Peripheral light and Indoor Exhaust Fans) | 500 | Mtr. | 135 | #NAME? | 67500
(v) | 1 core x 2.5 sqmm, Cu. Conductor (for protective earth) | 180 | Mtr. | 7 | #NAME? | 1260
11.9 | Cable tray
a) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 300 mm width & 100 mm height comprising all required standard accessories. | 16 | Mtr. | 442 | #NAME? | 7072
b) | Providing & erecting Hot dipped galvanized ladder type cable tray manufactured from 16 swg (1.6 mm thick) GI sheet of 150 mm width & 100 mm height comprising all required standard accessories. | 130 | Mtr. | 354 | #NAME? | 46020
11.1 | Hume pipe for Road crossings for Cable & Earth Strip crossing
a) | RCC Hume Pipe, 2000 mm Long, 150 mm Dia | 8 | No. | 223 | #NAME? | 1784
b) | Collars for RCC Hume Pipe | 4 | No. | 60 | #NAME? | 240
c) | Laying of RCC Hume pipes | 8 | No. | 33 | #NAME? | 264
11.11 | MS Chequrred plate of 6mm thick and 5.sq.meter area for trenches. | 250 | Kg | 110 | #NAME? | 27500
11.12 | Supplying and erecting exhaust fan heavy duty 440 V A.C. 50 cycles 900 RPM 375/380 mm complete erected in position. | 1 | No. | 4098 | #NAME? | 4098
| TOTAL CARRIED TO BILL XID SUMMARY |  |  |  |  | 12141111
Part 2D : CIVIL WORKS FOR GROUND LEVEL RESERVOIR CHHOKANAHALLI
BILL OF QUANTITIES - XIID : OFFICE BUILDING WORKS
12.1 | Earthwork in excavation of foundation of structures in all types of soil excluding hard rock by mechanical means as per drawing and technical specification, including setting out, providing shoring, strutting and bracing, removal of stumps and other deleterious matter, dressing of sides and bottom, filling back the excavated earth to the extent required and utilising/transporting/disposal the remaining earth including coast of labour, materials,lead and HOM of machineries etc., complete as per specifications. | 251 | Cum | 183 | #NAME? | 45933
12.2 | Earthwork in excavation by manual means for structures in all types of soil excluding hard rock, including dressing the bottom and sides of pits and trenches, stacking the excavated soil clear from edges of excavation with lead upto 50m after breaking of clods complete as per specifications
a) | 0 to 1.5 m depth | 55 | Cum | 438 | #NAME? | 24090
b) | 1.5 to 3 m depth | 55 | Cum | 438 | #NAME? | 24090
c) | 3 to 4.5 m depth | 165 | Cum | 438 | #NAME? | 72270
12.3 | Excavation for foundation of all structures, either in pits or trenches 1.5 m and above in width, in hard rock by chiselling and / or wedging where blasting is prohibited, including stacking the excavated stuff clear from the edge of excavation with lead upto 50m including cost of explosives, labour, HOM of equipment complete as per specifications
a) | 0 to 1.5 m depth | 55 | Cum | 1093 | #NAME? | 60115
b) | 1.5 to 3 m depth | 143 | Cum | 1093 | #NAME? | 156299
c) | 3 to 4.5 m depth | 55 | Cum | 1093 | #NAME? | 60115
12.4 | Providing and laying in position plain cement concrete of mix 1:3:6 with OPC cement content at 220Kgs using 40 mm and down size graded granite metal course aggregates @0.84cum and the fine agregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications. | 83 | Cum | 6755 | #NAME? | 560665
12.5 | Filling available excavated earth (excluding rock ) in sides of foundations upto plinth in layers not exceeding 20 cms. in depth, compacting each deposited layer by ramming after watering with all leads and lifts and including cost of all labour complete as per specifications. | 348 | Cum | 73 | #NAME? | 25404
12.6 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons.(Type F1 finish) | 121 | sqm | 729 | #NAME? | 88209
12.7 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per specifications. (Type F2 finish) | 221 | sqm | 729 | #NAME? | 161109
12.8 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications. (Type F2 finish) | 469 | sqm | 729 | #NAME? | 341901
12.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs, landing, balconies and likes thickness upto 200 mm including cost of all materials, labours, complete as per specifications. (Type F2 finish)
a) | 0-3.5m height | 310 | sqm | 729 | #NAME? | 225990
12.10 | Providing and laying in position reinforced cement concrete of design mix M25 as per specifications using 20 mm and down size graded granite metal course aggregates and the fine agregates with superplastisiser conforming to IS9103-1999 reaffirmed-2008, machine mixed, concrete laid in layers not exceeding 15 cms, thick, well compacted, in foundation and plinth , ground floor level for roof slabs, staircase, lintels, etc, including cost of all materials, labour, HOM of machinery, curing complete as per specifications | 175 | Cum | 7912 | #NAME? | 1384600
12.11 | Providing TMT bars of Fe 500 grade steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design (laps and wastage shall not be measured and paid) cost of materials, labour, HOM of machinery complete as per specifications. | 17 | MT | 67665 | #NAME? | 1150305
12.12 | Providing and constructing precast concrete solid blocks with compressive strength not less than 35kg. per sqm with cement mortar 1:4 masonry (quoin, Jamb, closer blocks) with solid concrete blocks of size 40x20x20 cms conforming to IS.2185/ 1965 in superstructure including cost of materials, labour charges, double scaffolding, curing complete as per specifications. | 741 | sqm | 1454 | #NAME? | 1077414
12.13 | Providing plastering to masonry including providing and removing scaffolding rounding of all corners whever required, smooth rendering curing etc complete as per specifications with burnt brick masonry plain plastering 12mm thick in CM 1:4 with lime rendering (internal) | 1179 | sqm | 283 | #NAME? | 333657
12.14 | Providing plastering to masonry including providing and removing double scaffolding rounding of all corners whever required smooth rendering curing etc., complete as per specifications with burnt brick masonry plain plastering 20mm thick in CM 1:4 (external) | 650 | sqm | 336 | #NAME? | 218400
12.15 | Providing and applying painting in two coats with plastic emulsion paint of approved brand on wall surface to give an even approved shade after thoroughly brushing the surface, free from mortor drops and other foreign matter including preparing the surface even and sand paper smooth, cost of materials, labour, complete as per specifications. (internal) | 1179 | sqm | 178 | #NAME? | 209862
12.16 | Providing and finishing external walls in two coats with waterproof cement paint of approved brand and shade to give an even shade after throughly brooming the surface to remove all dirt and loose powdered material, free from mortar drops and other foreign matter cost of materials, labour, complete as per specifications.(external) | 650 | sqm | 175 | #NAME? | 113750
12.17 | Providing and laying flooring and steps fine machined polished granite stone slabs of approved colour 20mm thick on cement mortar bed 1:6, 20mm thick, and, joints finished with cement mortar 1:3 over existing cement concrete bed ,including cost of materials, labour, curing complete as per specifications. | 275 | sqm | 4372 | #NAME? | 1202300
12.18 | Providing and fixing ceramic tiles (non skid) of size 400x400mm for flooring laid on a bed of 20mm thick cement mortar 1:3 mix flush pointing with white cement mixed with matching colour pigment including curing, cleaning,etc., complete.The work includes cost of all materials,mortar,labour charges for all items of work,hire charges for equipment,etc., complete as per specifications.
a) | For wash room in Office building | 55 | sqm | 1325 | #NAME? | 72875
12.19 | Providing dado, rises of steps with colour glazed tiles on 10mm thick cement plaster 1:3 and jointed with white cement slurry over rough plaster surface ( excluding cost of rough plastered surface which should be measured and paid separately) using glazed tiles of approved make and size including cost of materials, labour, complete as per specifications.
a) | For Office Room | 28 | sqm | 1299 | #NAME? | 36372
12.20 | Providing, fabricating and fixing in position anodised aluminum doors using following aluminum sections mat or glossy finish, outer frame of section 101.6 x 44.45 x 3.18 mm at 2.404 Kg/m, door shutters vertical section - 44.62 x 44.45 x 3.00mm at 1.426 Kg/m, bottom section 114.3 x 44.45 x 3.18mm at 2.646 kg/m, top section 47.62 x 44.45 x 3.00mm at 1.426 kg/m, middle section 49.91 x 44.45 x 3.00mm at 1.495 Kg/m, glazing clips 19 x 17.3x 11mm x 0.90 mm thick at 0.124 kg/m, all sections anodised to 12 to 15 microns. Cut to length, joint mitred corners grinded, shutters pivoted opening arrangement with h eavy duty aluminum alloy automatic door closer, floor mounted, providing and fixing standard approved accessories such as aluminum handle, for full width or length, tower bolts, lock pivots, PVC or rubber gaskets with 5.5 mm thick plain glass for top and bottom panel, aluminum sections treated for removal of rust, coated with greasy material for non adherence of mortar or any sticky material, the assembled frame fitted with corner angles, strips and fitted with rawl plugs, or teak wood gutties, to RCC columns, or masonry sides, including cutting, chiselling, and makin good the surface, all the frames thoroughly cleaned free from rust, scaleor dirt including cost of all materials, fixtures, labour, HOM of machinaries, etc complete. as per specifications | 9 | sqm | 9472 | #NAME? | 85248
12.21 | Providing and fixing in position anodized aluminium windows and ventilators as per approved drawings with sliding shutters using double track window frame section of size 61.85x31.75mm. with 1.2mm thick, bottom section weight 0.695 kg/m, sides and top sections 1.3 mm. thick weight 0.659 kg/m; and shutter comprising top and bottom section of size 40mmx18mm, 1.25mm thick 0.417 kg./m; shutter outer side 40mmx18mm, 1.25mm.thick weight 0.417 kg/m, shutter interlock section 40mmx26.7mm, 1.1mm thick, weight 0.469 kg/m. the shutters mounted on nylon rollers with approved quality of fixtures such as aluminium handles tower bolts etc.; and providing and fixing 5.5mm. thick plain glass for shutters fitted with rubber beading aluminium sections anodised 12 to 15 microns, including cutting to required length, joints mitred subdividing the frame tenonned and rivetted in the assembled frame stiffened with end clips at corners angles etc., and fixed to the walls, lintels, floor beams/cills as the case may be with necessary steel screws, raul plugs, or teak wood gatties including cutting masonry or concrete and making good the original surface using cement mortar, aluminium sections pretreated for removal of any rust and protection of further rust formation and coated with the greasy materials for non- adhesion of mortar and any other sticky materials, (this coating should be cleaned after installation) including cost of all materials, fixtures, labour and HOM of machinery complete as per specifications. | 20 | sqm | 7286 | #NAME? | 145720
12.22 | Providing and fixing mechanical gear type rolling shutters of approved make out of 18 gauge, 75mm wide cold rolled steel laths of convex corrugation, with side guides and bottom rail, with interlocking arrangement for steel laths by means of alternate clips, suspension shaft with High Tension coil type spring two numbers, mounted on specially designed pipe shaft, with bracket plates, guide channels, ball bearing arrangement for inside and outside locking with push & pull operations complete as per specifications with all lead and lift including cost of all civil works such cement concrete 1:2:4 and this shall be as approved drawings, specifications and direction including cost of conveyence, manufacturing, painting with enamel paint 2 coats over primer coat, cost of labour for all items of work, machinery,equipment and other incidental charges with all leads lifts. | 20 | sqm | 7286 | #NAME? | 145720
12.23 | Providing and laying in position yelahanka tiles of size 125 x 250mm of approved quality and make, over a bed of cement mortar 1:3 with thickness varying from 100mm to 25mm including weather proof course and pointed with cement mortar 1:3 mix with red oxide including curing cost of materials, labour complete as per specifications. | 318 | sqm | 1403 | #NAME? | 446154
12.24 | Providing and fixing skirting of 300mm high using prepolished water cut/gang saw of 19mm thick grey granite 0.5mm wide chamfered width and depth and fixing in CM 1:4 of 20mm thick after chipping the walls, etc., including cost of all materials, mortar,labour,curing,etc., complete as per specifications. | 59 | sqm | 4372 | #NAME? | 257948
12.25 | Providing and laying 230 mm thick rubble packing in plinth with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, including spreading 12 mm layer of stone grit on top, etc., complete for all building works as per drawings, details and specifications. | 80 | Cum | 3098 | #NAME? | 247840
12.26 | Providing and fixing 304- grade Stainless steel handrails of 14 gauge pipe for ramps or staircase are made out of stainless steel hollow pipes, using 50mm dia for verticals @ 1.60mtr c/c are fixed to the rams or steps by drilling with bolts and 100mm dia MS base plates 10mm gauge for fixing of vertical pipes 4 nos anchor bolts & 40mm dia pipes are fixed horizontally for 2 rows top one pipe are fixed with vertical pipes another one are fixed with elbows & 25mm dia pipes are fixed horizontally for 2 rows with elbow top measure @ equal intervals including cutting, welding, bending wherever necessary with suitable caps @ tops, bottoms, corners finishing with mat/shining etc., completeincluding cost and conveyance of all materials, labour for all items of work, HOM of euipment with all lead and lift, loading and unloading, transportation charges and all other incidental charges etc., complete as per specification and directions of the Engineer-in-charge of the work. Ramps or staircase for physically challenged. | 10 | RM | 2889 | #NAME? | 28890
12.27 | Providing and fixing white vitreous china clay, water closet European type (Pedestal type, P-trap) with black solid plastic seat and lid, CP brass hinges, rubber buffers, 10 litre low level, P.V.C flushing cistern (all are approved make) with fittings, SS brackets, 40mm diameter flush bend with fittings and clamps, overflow arrangements with specials and 25mm mosquito proof coupling of approved design, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 14572 | #NAME? | 29144
12.28 | Providing and fixing white vitreous china clay, flat back wash basins of size 550 mm x 400 mm with a pair of 15mm C.P brass pillar taps with SS brackets, 32mm C.P brass waste of standard pattern, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 8743 | #NAME? | 17486
12.29 | Providing and fixing white vitreous china clay, flat back, lipped front urinal basin of 430x260x350mm in the range of three with 7.5 litres PVC automatic flushing cistern, SS brackets, standard flush pipe and C.P brass spreaders with brass unions and G.I clamps painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | Nos. | 7286 | #NAME? | 14572
12.30 | Providing and fixing in position brass bib cock of aproved quality 15mm nominal bore including cost of all materials, labour and HOM of equipments with all leads complete as per specifications. | 3 | Nos. | 1458 | #NAME? | 4374
12.31 | Providing brick masonry inspection chambers, rectangular in size 90 cm x 45 cm and upto 1.5 m depth on sewer line , with 230 mm brick wall in cement mortar (1:2), plastered both inside and outside with 20 mm thick cement mortar (1:2),including 1.6 m x 1.2 m x 290 mm thick cement concrete 1:2:4 in haunches as per standard plan including excavation, backfilling the excavated sides and removing surplus earth and with heavy duty C.I. cover and frame and with M.S. steps fixed in cement mortar with cement and sand filleting. | 2 | Nos. | 26223 | #NAME? | 52446
12.32 | Same for above item 12.31 above but for depth greater than 1.5 m and upto 3 m | 2 | Nos. | 38907 | #NAME? | 77814
12.33 | Constructing circular type manhole 1500mm internal dia at bottom, 525mm dia at top, in wire cut burnt brick masonry with 1:5 cement mortar, cement plaster 1:3, finish with a floating coat of neat cement, RCC 1:2:4 top slab using 20mm and downsize granite metal, foundation concrete, M7.5 using 40mm and downsize granite metal and making channels in cement concrete M15 using 20mm and downsize granite metal, neatly finished curing, fixing CI cover complete including external, footrests and 12mm thick cement plaster on the external surface, cost of materials, labour charges, HOM of machineries complete as per specifications. | 1 | Nos. | 75965 | #NAME? | 75965
12.34 | Providing and fixing PVC Nahani trap of approved make conforming to ISI specifications and construction of cistern in M-15 as per directions. (rate inclusive of cost of materials and fixtures and conveyance of materials to work spot).
a) | 12.5cms X 7.5cms | 3 | Nos. | 875 | #NAME? | 2625
12.35 | Providing stoneware gully trap of approved quality and make fixing in M-15 and plastering with CM 1:3 wherever necessary. (rate includes cost of all materials, fixtures and lead). With 100mm outlet.
a) | 10cms X 10cms | 2 | Nos. | 1458 | #NAME? | 2916
12.36 | Providing and fixing 75 mm dia PVC slotted vent cowls conforming to IS 3989 with necessary fixtures and as directed by Engineer. | 2 | Nos. | 729 | #NAME? | 1458
12.37 | Providing and fixing white glazed 'P' trap as per IS 2556 (Part 7) 100 mm dia with SS grating 10 mm thick etc., complete. | 2 | Nos. | 1458 | #NAME? | 2916
12.38 | Providing and fixing cast copper alloy stop valves, polished bright, conforming to and as per IS 781.
a) | 25 mm dia. | 2 | Nos. | 729 | #NAME? | 1458
b) | 20 mm dia. | 2 | Nos. | 729 | #NAME? | 1458
c) | 15 mm dia. | 2 | Nos. | 729 | #NAME? | 1458
12.39 | Providing and fixing SS towel rail 740mm length, 20mm dia with C.P brackets, fixed to wooden cleats with C.P brass screws including cost of materials, labour complete as per specifications. | 4 | Nos. | 2186 | #NAME? | 8744
12.40 | Providing and fixing best quality SS liquid soap bottle holders of approved make with SS brackets, screws, rawl plugs, etc. complete. | 4 | Nos. | 1458 | #NAME? | 5832
12.41 | Providing and fixing 600x450 bevellead edge mirror of superior glass with 6mm hard board backing and fixed to wooden cleats with C.P screws, washers, including cost of materials, labour complete as per specifications. | 4 | Nos. | 7286 | #NAME? | 29144
12.42 | Providing and fixing UPVC water pipes and fittings 'B' class pressure rating of 10kg/cm2 conforming to IS 13592 and IS14735, with all necessary fixtures and bends, including testing the line as specified,etc.,complete.
a) | 25 mm dia. | 39 | RM | 292 | #NAME? | 11388
b) | 20 mm dia. | 28 | RM | 219 | #NAME? | 6132
c) | 15 mm dia. | 28 | RM | 146 | #NAME? | 4088
12.43 | Providing and Fixing PVC soil waste and vent pipes 100 mm diameter - 10kg/cm2 with spun yarn soaked in cement slurry and cement mortar 1:2 including cost of materials, labour, testing complete as per specifications. | 33 | RM | 875 | #NAME? | 28875
12.44 | Providing and fixing PVC pipes of approved make and 150 mm dia - 10kg/cm2 conforming to IS 651, including all necessary fixtures and bends, including excavation, backfilling, testing etc., complete as per specification. | 33 | RM | 1284 | #NAME? | 42372
12.45 | Providing and fixing 100 mm dia - 10kg/cm2 PVC rain water pipes as per IS: 4984 including all fixtures such as brackets, bends etc.as directed by the Engineer. | 55 | RM | 315 | #NAME? | 17325
12.46 | Providing and fixing cast iron bell mouth rain water outlets including MS grating, etc., complete as directed by Engineer.
a) | 100mm Dia. | 4 | Nos. | 1458 | #NAME? | 5832
12.47 | Providing and hoisting to the position and fixing polyethelene plastic water storage tank of 500 litres of approved make with mosquito proof jali frame and cover 450mm dia. with locking arrangement, including copper ball cock with brass arm including washout plug, overflow GI pipe etc., complete. with lead and lift. | 1 | Nos. | 10200 | #NAME? | 10200
12.48 | Indoor Lighting DB: Supply, Transportation, Installation, testing & Commissioning of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos DP outgoings and for 1 No 4 pole Incomer with IP-54 enclosure, bottom entry cable, necessary accessories like wiring, contactors, terminal block, aux. relays, timer etc complete. a) Incomer: 63A, TPN, MCCB and 100mA, RCCB b) Outgoings: 6-32A, DP, MCB - 8 Nos and 32A TPN MCB - 3Nos c) Supplying and erecting extended rotary handle for MCCB with adjustable telescopic rod 63A MCCB - 1No. d) Supplying, erecting & marking SPMCB 5A in provided distribution board - 3Nos. e) Supplying & erecting LED type indicating pilot lamp with suitable LED colours, 230 / 250V on provided box / panel with necessary material, wiring & connections etc. - 6Nos. f) Supplying and erecting panel mounting type digital ammeter having three and half digit LED display, external CT operated, calibrated for suitable to operate on 500V, 0 to 1000A AC supply with necessary PVC wire leads and lugs and mounting hardware on provided panel complete with calibration certificate from manufacturer.. - 1No. g) Supply and Fixing of Current Transformerwith all necessary support in existing panel including connection etc. 60/5A, 5 VA , class 1 accuracy.- 3Nos. | 1 | Nos. | 41716 | #NAME? | 41716
| The cost for fabrication panel, Copper / Al busbars, interconnecting cables, mounting fasterners, terminal box etc. Installation, Commissioning and transportation | 1 | Set | 14601 | #NAME? | 14601
12.49 | Supplying, Erection & Termination of XLPE armoured cable copper conductor continuous 5.48 sq.mm. (12 SWG) GI earth wire complete erected with glands & lugs, on wall/trusses/pole or laid in provided trench/pipe as er PWD specifications.
a) | 4Cx6 sq.mm (Indoor Ltg DB, 3phase sockets) | 100 | Mtr. | 280 | #NAME? | 28000
b) | 2Cx4 sq.mm (Indoor Lighting Ckts, 1-ph sockets, 1-ph Exhaust Fans etc.) | 200 | Mtr. | 138 | #NAME? | 27600
12.50 | Lighting System:
a) | Supply, installation, testing & commissioning of Light Luminares complete with: a) All accessories including mounting for fully functioning of fixture (Indoor & Outdoor). b) Earthing of fittings. c) Lamp of suitable wattage.
(i) | Supply, transportation and fixing of 36W Recessed / Surface mounting 2' x 2' (600x600 mm) LED luminaire made of CRCA sheet housing with powder coated with acrylic diffuser, Constant current Driver as per IS: 15885 (Part 2/ Sec 13) : 2012, With System lumen output ≥3200lm operating voltage range of 150 to 265 Volts AC, P.F > 0.9, Surge protection: 2KV, THD<10%, with high power LED's having efficacy of > 120 lumins / watt, CCT: 3000K - 5700K, minimum CRI>70, .etc.,, complete. - Decorative Type (Indoor Areas) | 36 | Nos. | 4761 | #NAME? | 171396
(ii) | Supply, transportation and fixing of 36W Recessed / Surface mounting 2' x 2' (600x600 mm) LED luminaire made of CRCA sheet housing with powder coated with acrylic diffuser, Constant current Driver as per IS: 15885 (Part 2/ Sec 13) : 2012, With System lumen output ≥3200lm operating voltage range of 150 to 265 Volts AC, P.F > 0.9, Surge protection: 2KV, THD<10%, with high power LED's having efficacy of > 120 lumins / watt, CCT: 3000K - 5700K, minimum CRI>70, .etc.,, complete.. - Industrial Type (Indoor Areas) | 18 | Nos. | 4761 | #NAME? | 85698
(iii) | Emergency Lighting: Supply & Fixing of Rechargeable emergency lamp (600 mm fluorescent lamp) or LED lamp with accessories complete | 9 | Nos. | 2703 | #NAME? | 24327
b) | Fixing of Fittings
(i) | Fixing all types & all capacities fluorescent/ CFL fittings Indoor on the wall /ceiling/rafters/gridders using 23 / 0.76 " twin twisted PVC insulated wires. | 62 | Nos. | 216 | #NAME? | 13392
12.51 | Supply and transportation of LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 110 lm/W and junction temprature < 70°C, with Ingrees protection IP66, Luminaire performance complies to IS 10322 (Part 5 / Sec-3), Driver surge protection 4KV, external Surge protection 10 KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete
a) | 60W (Peripheral Lighting) | 8 | Nos. | 5018 | #NAME? | 40144
b) | Supplying and erecting Peripheral light bracket for erection of single fitting made from 40 mm. dia ‗B‘ class G.I. pipe 1.0 m in length along with pole cap of 300 mm length 100 mm dia duly welded | 8 | No. | 765 | #NAME? | 6120
c) | Supply & Erection of Plug, Sockets, Switches with accessories and enclosure
i) | One/Two way piano type switch 6A | 30 | Nos. | 92 | #NAME? | 2760
ii) | 3 pin plug socket 6A | 15 | Nos. | 139 | #NAME? | 2085
iii) | Piano type switch 16A | 15 | No. | 213 | #NAME? | 3195
iv) | 3 pin plug socket 16A | 14 | No. | 152 | #NAME? | 2128
d) | Supplying and erecting unbreakable concealed type modular switch box with double mounting plate for 6 module duly erected flush to wall with required chiselling and finishing with cement mortar / POP as per required to match the background. | 14 | Nos. | 190 | #NAME? | 2660
12.52 | Supply of ISI marked 32mm outer dia medium grade with IS:9537 part 3 FRLS regid PVC conduit pipe.
a) | Primary point from lighting panel to modular switch box for Lighting and ceiling fan circuits | 200 | Mtr. | 85 | #NAME? | 17000
b) | Point wiring from lighting panel to modular switch box for receptacle circuits | 100 | Mtr. | 77 | #NAME? | 7700
c) | Secondary point from tapping point to Light and fan points
i) | Short point (not exceeding 3m) | 50 | Mtr. | 77 | #NAME? | 3850
ii) | Medium point above 3m and up to 6m | 100 | Mtr. | 77 | #NAME? | 7700
iii) | Long point above 6m and up to 10m | 100 | Mtr. | 77 | #NAME? | 7700
d) | Supply of 2.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 100 | Mtr. | 27 | #NAME? | 2700
e) | Supply of 1.5 sq.mm FRLS / HFFR / ZHFR PVC insulated 1100V grade as per IS : 694 / 1990 specification for Copper cable. | 200 | Mtr. | 18 | #NAME? | 3600
f) | Supplying and erecting five star rated energy saving Ceiling fan 230 V A.C. 50 cycles 1200 mm complete erected in position | 12 | Nos. | 3091 | #NAME? | 37092
g) | Supplying and erecting exhaust fan heavy duty 440 V A.C. 50 cycles 900 RPM 375/380 mm complete erected in position. | 6 | Nos. | 4098 | #NAME? | 24588
| TOTAL CARRIED TO BILL XIID SUMMARY |  |  |  |  | 10037019

## Summary - Chokkanahalli
CONTRACT NO. CP-13
Part 2D : CIVIL AND ELECTRO MECHANICAL WORKS FOR GROUND LEVEL RESERVOIR AT CHHOKANAHALLI
SUMMARY OF BILL TOTALS
Bill No. |  | Amount in Rs.
ID | Earthworks | 20885065
IID | Concrete and Allied works | 319569273
IIID | General Building Works | 52228420
IVD | Water Supply & Sanitary Works | 1790286
VD | Structural Steel Works | 2339460
VID | Roadworks | 29171697
VIID | Pipeworks, Valves and Specials | 12455409
VIIID | Mechanical works | 4541135
IXD | Instrumentation works | 1365073
XD | Electrical works | 1713436
XID | Miscellaneous works | 12141111
XIID | Office building works | 10037019
TOTAL CARRIED TO GRAND SUMMARY |  | 468237384

## SOD
SCHEDULE OF DAYWORKS
Item No. | Description | Quantity | Unit | Rate in figures (Rs.) | Rate in Words (Rs.) | Amount (Rs.)
Note:The Contractor is to enter below the fully inclusive rates which he will charge for works carried out on a day work-basis. These rates are to cover for all overtime, subsistence and condition payments, transport of labour, supervisory cost and expenses, overhead charges and profit, waste, fuel, power, water and other consumable stores:use of all hand and pnemuatic tools, light and non-mechanical plant:use of rail tracks, roads, scaffolding, staging, pumps, pipelines, hoists, derricks or cableways erected or in the operation for other purpose and used incidentally: spares and maintanance to plant: all as necessary for the purpose and efficient carrying out of the dayworks ordered. All quantites are provsional.
1 | Labour
(a) | Unskilled Labour(man) | 8000 | Man Day | 804 | #NAME? | 6432000
(b) | Unskilled Labour(woman) | 1000 | Man Day | 804 | #NAME? | 804000
(c) | Tradesmen's helper | 2000 | Man Day | 804 | #NAME? | 1608000
(d) | Carpenter and jointer | 200 | Man Day | 963 | #NAME? | 192600
(e) | Plumber | 1000 | Man Day | 963 | #NAME? | 963000
(f) | Bricklayer | 200 | Man Day | 963 | #NAME? | 192600
(g) | Drain Layer and pipe fitter | 1000 | Man Day | 880 | #NAME? | 880000
(h) | Electrician | 400 | Man Day | 963 | #NAME? | 385200
(i) | Fitter | 1000 | Man Day | 963 | #NAME? | 963000
(j) | Mason | 500 | Man Day | 963 | #NAME? | 481500
(k) | Bar benders and fixer | 1000 | Man Day | 963 | #NAME? | 963000
(l) | Watchman | 1000 | Man Day | 963 | #NAME? | 963000
(m) | Ganger | 1400 | Man Day | 880 | #NAME? | 1232000
(n) | Chainmen and other personnel to assist Engineer's staff | 400 | Man Day | 880 | #NAME? | 352000
(o) | Gascutter | 400 | Man Day | 880 | #NAME? | 352000
(p) | Welder | 1000 | Man Day | 880 | #NAME? | 880000
2 | Materials
(a) | Diesel engine oil | 8000 | Litre | 94 | #NAME? | 752000
(b) | Welding rods | 12000 | No. | 7 | #NAME? | 84000
3 | Construction Equipment
(a) | Portable compressor with one tool and required length of hose 3 m3/min | 1200 | Hour | 1479 | #NAME? | 1774800
(b) | Mobile crane (10 to 15 tonnes capacity) | 4000 | Hour | 1109 | #NAME? | 4436000
(c) | Dumper / Tipper-5 cum capacity | 2800 | Hour | 826 | #NAME? | 2312800
(d) | Generating set (6 kW) (approx.) | 600 | Hour | 345 | #NAME? | 207000
(e) | Electric welding set including ancillary equipment and consumables | 1000 | Hour | 616 | #NAME? | 616000
(f) | -Do- oxy-acetylene gas cutting / gauging | 500 | Hour | 1109 | #NAME? | 554500
(g) | Loading shovel (1 m3 capacity) | 600 | Hour | 493 | #NAME? | 295800
(h) | Dewatering pump with required suction hose, foot valve and strainer, delivery hose etc.
| (i) 5 HP | 4000 | Per day (8 hr shift) | 1848 | #NAME? | 7392000
| (ii) 7.5 HP | 4000 | Per day (8 hr shift) | 2218 | #NAME? | 8872000
| (iii) 15 HP | 4000 | Per day (8 hr shift) | 3080 | #NAME? | 12320000
| (iv) 30 HP | 4000 | Per day (8 hr shift) | 6160 | #NAME? | 24640000
(i) | Concrete mixer (0.4/0.3 m3 capacity) | 1000 | Hour | 308 | #NAME? | 308000
| SUB TOTAL |  |  |  |  | 82208800 | #REF!
FEE (% OF SUB TOTAL)
TOTAL CARRIED TO GRAND SUMMARY | [5 empty] | 82208800 | #REF!

## GRAND Summary
CONTRACT NO. CP-13
GRAND SUMMARY
Item. No. | Description | Amount in Rs.
1) | Part 2A : Civil and Electro Mechanical Works for Ground Level Reservoir at Lingadernahalli | 152693721
2) | Part 2B : Civil and Electro Mechanical Works for Ground Level Reservoir at Singapura | 509459384
3) | Part 2C : Civil and Electro Mechanical Works for Ground Level Reservoir at Vasudevpura | 141069461
4) | Part 2D : Civil and Electro Mechanical Works for Ground Level Reservoir at Chhokanahalli | 468237384
5) | Total of Items 1, 2, 3 & 4 | 1271459950
6) | Schedule of Dayworks | 82208800
7) | Provisional sum, Physical contingencies | 89731250
Total Bid Amount (Item 5 + 6 + 7) |  | 1443400000
Total Bid amount in words : Rupees One Hundred Forty Four Crore Thirty Four Lakh Only
Dated this 28th day of June, 2020
Signature _____________________ (S CHANDRAEASWARAN) in the capacity of Joint General Manager and Head, Urban Water & Water Management Segment, Water & Waste Water Strategic Business Group, duly authorised to sign for and on behalf of Larsen and Toubro Limited