## Grand Summary
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
GRAND SUMMARY
Page | Bill No. | Description | Amount (Rs.)
I Earthwork | I | Earthworks | 832996950
II Concrete | II | Concrete and Allied works | 1040299360
III-A Pipelines | III | Pipeline, Specials and Appurtenances | 6803993832
IV Pipe Bridges | IV | Pipe Bridge crossings across Bheema and Arkavathi | 149287135
V One Surge tank | V | Oneway Surge tank | 32749685
VI.NH Crossings | VI | NH crossings | 133830900
VII-Electrical | VII | Electrical works | 2078828
| A | Sub Total of Bills I to VII | 8995236690
| B | Discount Offered | NIL
SOD | C | Schedule of Dayworks | 11528677.5
| D | Total (Item A - B + C) - Evaluated Bid Price (Excluding Provisional sum, Physical contigencies) | 9006765367.5
| E | Provisional sum, Physical contingencies | 565021868
| Total Bid Amount (Item D + E) |  | 9571787235.5

## I Earthwork
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
BILL OF QUANTITIES - I : EARTHWORKS
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
2 | 1.1 | Earthwork excavation for pipeline trenches, anchor/thrust blocks, saddle supports, valve chambers, etc. in all types of soils exclusive of hard rock, by mechanical / & manual means including dressing sides,ramming of bottoms, providing barricading,shoring,strutting,dewatering, disposing off excess materials away from the site of work with all leads and lift,etc. complete all as per specifications.
3 | (a) | 0 to 2 m depth | 431165 | Cum | 175 | 75453875
3 | (b) | 2 to 4 m depth | 411035 | Cum | 250 | 102758750
3 | (c) | 4 to 6 m depth | 96620 | Cum | 325 | 31401500
3 | (d) | > 6 m depth | 1846 | Cum | 375 | 692250
2 | 1.2 | Earth work excavation for pipeline trenches, anchor/thrust blocks, saddle supports, valve chambers, etc in hard rock by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading,danger lighting shoring, strutting, dewatering,disposing off excess materials away from the site of work with all leads and lift etc. complete all as per specifications.
3 | (a) | 0 to 2 m depth | 32920 | Cum | 1700 | 55964000
3 | (b) | 2 to 4 m depth | 32920 | Cum | 1800 | 59256000
3 | (c) | 4 to 6 m depth | 82300 | Cum | 1900 | 156370000
3 | (d) | > 6 m depth | 16450 | Cum | 2000 | 32900000
2 | 1.3 | Backfilling around pipeline trenches and foundations of structures, etc.,with approved excavated soil including depositing in layers not exceeding 200 mm, watering, ramming manually and/or compaction with mechanical compaction machines to 95% Modified Proctor density,etc., complete all as per specifications. | 624545 | Cum | 115 | 71822675
2 | 1.4 | Providing bedding for pipeline trenches in rock reaches with well graded sand as per drawing and complete with all lead and lift as per specifications for Class N Bedding. | 33940 | Cum | 800 | 27152000
2 | 1.5 | Cutting road surface for pipeline trenches and disposing off the excavated stuff with all leads and lifts as directed including barricading, danger lighting etc. complete in the following classifications.
3 | (a) | Cutting macadam road | 1876 | Cum | 950 | 1782200
3 | (b) | Cutting asphalt road | 65510 | Cum | 1000 | 65510000
3 | (c) | Cutting cement concrete road | 4220 | Cum | 1200 | 5064000
2 | 1.6 | Reinstatement of roads in item 1.5 as per drawings and specifications as directed.
3 | (a) | Macadam road | 1876 | Cum | 2200 | 4127200
3 | (b) | Asphalt road | 100785 | Sqm | 1300 | 131020500
3 | (c) | Cement concrete road | 8440 | Sqm | 1300 | 10972000
2 | 1.7 | Excavation in filled up earth in existing structures including dewatering, diverting water courses if required, trimming of bottom and disposing of excavated materials with all leads and lifts complete as directed and as per specifications. | 2500 | Cum | 300 | 750000
| SUB TOTAL |  |  |  |  | 832996950
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 832996950

## II Concrete
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
BILL OF QUANTITIES - II : CONCRETE AND ALLIED WORKS
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
2 | 2.1 | Providing and laying in position plain cement concrete of mix 1:3:6 with OPC cement content at 220Kgs using 40 mm and down size graded granite metal course aggregates @0.84cum and the fine agregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth for levelling course, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications. | 2290 | Cum | 6500 | 14885000
2 | 2.2 | Providing and laying in position reinforced cement concrete of design mix M20 as per specifications using 20 mm and down size graded granite metal course aggregates and the fine agregates with superplastisiser, machine mixed, concrete laid in layers not exceeding 15 cms, thick, vibrated,well compacted, including cost of all materials, labour, HOM of machinery, curing complete as per specifications.
3 | (a) | Valve Chambers | 8690 | Cum | 7500 | 65175000
2 | 2.3 | Providing and laying in position cement concrete of mix 1:2:4 with OPC cement content at 240Kgs using 20 mm and down size graded granite metal course aggregates @0.878cum and the fine agregates @0.459cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, including cost of all materials, labour, HOM of machinery, curing complete as per specifications.
3 | (a) | Anchor/Thrust blocks, Concrete Encasement | 94893 | Cum | 5930 | 562715490
2 | 2.4 | Providing and laying in position reinforced cement concrete of design mix M25 as per specifications using 20 mm and down size graded granite metal course aggregates and the fine agregates with superplastisiser, machine mixed, concrete laid in layers not exceeding 15 cms. thick, vibrated, well compacted including cost of all materials, ,labour, HOM of machinery, curing complete as per specifications.
3 | (a) | Saddle supports | 6230 | Cum | 7624 | 47497520
2 | 2.5 | Providing TMT steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design including cost of materials, labour, HOM of machinery complete as per specifications. Fe 500 grade. | 3812 | MT | 68000 | 259216000
2 | 2.6 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons. (Type F1 finish) | 208900 | Sqm | 300 | 62670000
2 | 2.7 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per specifications. (Type F2 finish)
3 | (a) | Level from 0.00 to 3.50m | 1275 | Sqm | 450 | 573750
3 | (b) | Level from 3.50 to 4.50m | 1355 | Sqm | 450 | 609750
3 | (c) | Level from 4.50 to 5.50m | 1355 | Sqm | 450 | 609750
3 | (d) | Level from 5.50 to 6.50m | 7920 | Sqm | 450 | 3564000
2 | 2.8 | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. (Type F2 finish)
3 | (a) | Level from 0.00 to 3.50m | 17860 | Sqm | 350 | 6251000
3 | (b) | Level from 3.50 to 4.50m | 5350 | Sqm | 350 | 1872500
3 | (c) | Level from 4.50 to 5.50m | 5300 | Sqm | 350 | 1855000
3 | (d) | Level from 5.50 to 6.50m | 4667 | Sqm | 350 | 1633450
2 | 2.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications. (Type F2 finish)
3 | (a) | Beams Level from 0.00 to 3.50m | 2800 | Sqm | 450 | 1260000
3 | (b) | Beams Level upto 4.50m | 1500 | Sqm | 450 | 675000
3 | (c) | Beams Level upto 10m | 1500 | Sqm | 450 | 675000
2 | 2.10 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs,etc. including cost of all materials, labours, complete as per specifications. | 5410 | Sqm | 450 | 2434500
2 | 2.11 | Dismantling of existing structures in cement concrete in all grades,masonry,steel work, in foundation and/or above ground level including sorting the dismantled materials, disposal of unserviceable materials, stacking the serviceable materials, providing and removing scaffolding wherever nessecary cost of all labour charges, with all leads and lifts,complete as per specifications. | 540 | Cum | 450 | 243000
2 | 2.12 | Grouting with 1:3 (cement : sand) mortar for anchor bolt pockets, below base plates, pipe sleeves, pockets, holes, saddle supports etc., including roughening and cleaning of concrete surface, curing etc., complete. | 20 | Cum | 12500 | 250000
2 | 2.13 | Providing non-shrink grout of approved make for anchor bolt pockets below base plates, pipe sleeves etc., for ring girders as shown in Drawings. | 15 | Cum | 15000 | 225000
2 | 2.14 | Supplying and fixing PVC encapsulated CI rungs to shapes and at locations specified in drawings and complete as per specifications. | 1000 | kg | 95 | 95000
2 | 2.15 | Painting the surfaces of thrust/anchor blocks,valve chambers,saddle supports above ground level with cement paint of approved brand and shade after thoroughly brooming the surface to remove all dirt including cost of materials,labour, lettering for identification with paint complete as per specifications. | 14337 | Sqm | 50 | 716850
2 | 2.16 | Supply and fixing of manhole SFRC rings and covers as per IS Heavy duty to suit the existing damaged manhole & removing debries inside & outside the manhole with all leads & lift charges. | 167 | No. | 1400 | 233800
2 | 2.17 | Providing and fixing 6 mm thick graphited asbestos ferrobestos/Teflon with approved araldite to MS pipe over the saddle supports, as shown in drawings etc., complete as per specifications. | 1285 | Sqm | 1800 | 2313000
2 | 2.18 | Providing and fixing in position M20 grade (deisgn mix) precast RC covers with 20mm and down size aggregate of any size and shape for valve chamber including all precasting work,curing,reinforcement,formwork,etc., complete as per specifications and drawings. | 250 | Cum | 8200 | 2050000
| SUB TOTAL |  |  |  |  | 1040299360
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 1040299360

## III-A Pipelines
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
BILL OF QUANTITIES - III : PIPELINES,SPECIALS AND APPURTENANACES
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
Pipelines, Specials and Appurtenances
2 | 3.1 | Supply, freight and delivery of mild steel plates confirming to IS 2062 Grade B or any other equivalent international standard. The rate includes unloading of material at project site.
3 | (a) | Mild Steel Plates size 9500 mm x 2500 mm x 18 mm (length x width x thickness) | 17400 | Nos. | 188250 | 3275550000
2 | 3.2 | Fabricating, shop welding, transporting, handling, aligning, laying and jointing / welding of MS pipes of Plate welded pipes, IS 2062 Grade B for Plate welded. The rate also include loading and unloading, radiography of joints as specified and hydraulic testing of pipeline to specified pressure as per specifications and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings.
3 | (a) | 3001 mm internal diameter with 18 mm shell thickness | 43500 | RM | 57600 | 2505600000
2 | 3.3 | Providing, Fabricating, transporting, handling, aligning, laying and jointing/welding MS pipes inlcuding fixing collars, elbows, tees and other fittings to correct line and level in trenches as per the specifications and drawings. The rate to include transportation of pipes to site, loading, unloading, hoisting, lowering, marginal cutting wherever necessary, assembling, providing temporary supports etc., all with approved equipment complete. The rate also include radiography of field joints as specified and hydraulic testing of pipeline to specified pressure in stretches of length and test on completion using pumps which should be able to provide or resist specified test pressure, pressure gauges and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings.
3 | (a) | 1401 mm internal diameter with 10 mm shell thickness mild steel plate welded pipes, conforming to IS 2062 Grade B | 100 | RM | 33650 | 3365000
2 | 3.4 | Providing, fabricating, shop welding, handling, transporting, aligning, laying and jointing of MS specials of Plate welded pipes, conforming to IS 2062 Grade B for Plate welded. The rate include loading and unloading, radiography of joints as specified and hydraulic testing of specials to specified pressure and other necessary equipment, labour, operation charges etc., required for testing. Rate shall also include cost of retesting if necessary, complete in all respects as per specifications and drawings. | 2452380 | kg | 122 | 299190360
2 | 3.5 | Providing guniting (CM 1:3 over 50 x 50 mm weld mesh of 13 gauge) on the external surface of pipes and specials including supplying and fixing reinforcement as per specifications after cleaning the pipes including curing etc., at fabrication yard and guniting the field joints at site between two pipes after testing complete in all respects as per specifications.
3 | (a) | 3037 mm OD pipes and specials, 30 mm thick guniting | 413126 | Sq.m | 725 | 299516350
3 | (b) | 1421 mm OD pipes and specials, 30 mm thick guniting | 447 | Sq.m | 725 | 324075
2 | 3.6 | Providing food grade internal epoxy lining of 0.5 mm thick as per specifications to the internal surfaces of mild steel pipeline, fittings, specials etc., including surface preparation, machine lining, curing and testing / inspection etc., complete.
3 | (a) | 3000 mm ID pipes & specials to 3000 mm finished diameter, 0.5 mm thick internal epoxy lining | 415034 | Sq.m | 400 | 166013600
3 | (b) | 1400 mm ID pipes & specials to 1400 mm finished diameter, 0.5 mm thick internal epoxy lining | 440 | Sq.m | 400 | 176000
2 | 3.7 | Supply,installation, testing & Commissioning of 2600 mm PN 16 Manually operated Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for 3000mm diameter MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges. | 9 | No. | 9800000 | 88200000
2 | 3.8 | Supply,installation, testing & Commissioning of 1400 mm PN 16 electrically operated (motorised) Long Body, Double Flanged, Double eccentric Resilient seated Butterfly valve confirming to BS EN 593/IS 13095 for 1400mm diameter MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges. | 6 | No. | 4000000 | 24000000
2 | 3.9 | Supply,installation, testing & Commissioning of 1400 mm dia PN 16 Non return valves with necessary accessories for 1400mm diameter MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges. | 2 | No. | 3500000 | 7000000
2 | 3.10 | Supply, Delivery, testing, installation of 600 mm dia PN 25 (Scour purpose) DI double flanged Sluice Valves conforming to IS- 14846 (with up to date amendments, if any) including gear arrangements, for 600mm diameter MS pipes with necessary mating flanges,bolts & Gaskets and Bypass pipe & valve arrangement as per detailed specifications defined in Volume 2, The rate is inclusive of cost of mating flanges, bypass valve,bypass piping, bolts & nuts and rubber insertions complete ,excluding earthwork,Rates are incluisve of Labour Charges. | 22 | No. | 1500000 | 33000000
2 | 3.11 | Supply, Delivery, testing, installation of Ductile Iron (DI) 150 mm PN 16 Single/Double chamber Triple function Tamper Proof Kinetic Air valves with isolation valve -2 sets., mounted on a common MS fabricated stub arrangement of 300 mm dia. in Cluster Arrangement on pumping main header.Detailed Valve specifications shall be as defined in Volume 2,The rate is inclusive of cost of MS Stub arrangement, mating flanges, valve,bolts & nuts and rubber insertions complete,excluding earthwork,Rates are incluisve of Labour Charges. | 73 | Sets. | 55000 | 4015000
2 | 3.12 | Supply, Delivery, testing, installation of Ductile Iron (DI) 500 mm dia. PN 16 Spring loaded Vaccum breaker valve with Tamper Proof Kinetic Air valves, mounted on a common MS fabricated stub arrangement of 500 mm dia. on pumping header.Detailed Valve specifications shall be as defined in Volume 2. The rate is inclusive of cost of MS Stub arrangement, mating flanges, valve,bolts & nuts and rubber insertions complete,excluding earthwork,Rates are incluisve of Labour Charges. | 2 | Sets. | 950000 | 1900000
2 | 3.13 | Providing, supplying and fixing 3000 dia. PN16 SS 304 Expansion Bellows with Welded Ends as per specifications and drawings. The rate shall include transportation to site with all leads and lifts, aligning and jointing approved anti-corrosive paint etc., complete in all aspects. , Rates are incluisve of Labour Charges. | 16 | No. | 700000 | 11200000
2 | 3.14 | Providing and laying 600 mm internal dia MS pipes of 6 mm shell thickness conforming to IS 3589 in trenches outside 3000 mm ID pipeline scour valve chambers for draining. Item to include excavation, connecting to scour valve, backfilling the earth etc., complete. | 660 | RM | 12500 | 8250000
2 | 3.15 | Epoxy painting as per specifications to the external exposed surfaces of pipeline, fittings, specials over saddles including procuring approved primer and paints, surface prepartion, application and testing, inspection. | 2862 | Sq.m | 450 | 1287900
2 | 3.16 | Providing, fabricating and fixing at site, anchor bolts including anchorage assembly, composed of plates, MS insert plates on RC saddles including cost of materials, labour, threads, nuts, lock nuts, washers, pipe sleeves, welding, etc. Complete as per specifications and drawings. | 14 | MT | 100000 | 1400000
2 | 3.17 | Providing and fixing 6 mm thick graphited asbestos ferrobestos/Teflon with approved araldite to MS plate in saddle supports as shown in drawings etc., complete of approved manufacturer. | 1320 | Sq. m | 1600 | 2112000
2 | 3.18 | Providing, fabricating and transporting necessary holding down MS straps including bolts, nuts and washers etc., complete. | 10 | MT | 99854.7 | 998547
2 | 3.19 | Manufacturing, supplying and fixing of 600 mm dia. MS manholes as per specifications and drawings including transportation to the site of work, cutting of pipe and welding and fixing with pad plates with gaskets, bolts, nuts, washers, etc., and with 2 coats of painting over one coat of primer complete as per Specifications and Drawings. | 37 | No. | 35000 | 1295000
2 | 3.20 | Supplying and laying of 75mm dia UPVC conduit for optical fibre as per specifications. | 87000 | RM | 800 | 69600000
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 6803993832

## IV Pipe Bridges
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
BILL OF QUANTITIES - IV : PIPE BRIDGE CROSSINGS ACROSS BHEEMA AND ARKAVATHI
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
2 | 4.1 | Earth work excavation for foundation of structures by mechanical means in all types of soils exclusive of hard rock as per draiwng and technical specifications, including setting out,shoring,strutting,barricading,danger lighting,bracing,removal of stumps and other deleterious matter,dressing of sides and leveling of bottom of trenches to the extent required, disposing off excess materials away from the site of work,with all leads and lift, backfilling with approved excavated material,etc. complete all as per specifications. | 550 | Cum | 175 | 96250
2 | 4.2 | Earth work in excavation in ordinary rock not requiring blasting for foundation of structures as per drawing and technical specifications, including setting out, construction of shoring and bracing, removal of stumps and other deleterious matter, dressing of sides and bottom and backfilling with approved meterial,disposing off excess materials away from the site of work,with all leads and lift complete as per specifications. | 4446 | Cum | 200 | 889200
2 | 4.3 | Earth work excavation in hard rock by using mechanical means and trimming to proper slope,including depositing on bank, providing danger lighting and using sight rails and boning rods at every 100 meters, clearing vegetation, removing hedges, fences and walls, diverting water course, disposing off excess materials away from the site of work etc. complete and wherever necessary as identified by contractor and approved by Engineer. | 2030 | Cum | 1800 | 3654000
2 | 4.4 | Dismantling of existing structures like culverts, bridges, retaining walls and other structure comprising of masonary, cement concrete, wood work, steel work, including T&P and scaffolding wherever necessary. sorting the dismantled material, disposal of unserviceable material and stacking the serviceable material with all lifts complete as per specifications by Mechanical Means | 545 | Cum | 750 | 408750
2 | 4.5 | Providing and laying in position plain cement concrete 1:2:4 with OPC cement @ 240kgs, with crushed 40mm and down size graded granite metal coarse aggregates @ 0.84cum and fine aggregates @ 0.56cum, in foundation mechanically mixed, placed in foundation and compacted by vibration including curing for 14 days as per MORTH specifications and complete as per specifications. | 179 | Cum | 6500 | 1163500
2 | 4.6 | Providing and laying in position reinforced cement concrete in open foundation with cement design mix M30 as per specifications with 20mm and down size graded aggregates with superplastisiser in Open Foundation complete as per Drawing, MORTH and complete as per specifications. | 771 | Cum | 7000 | 5397000
2 | 4.7 | Sub-structure
3 | (a) | Providing and laying in position reinforced cement concrete of design mix M30 as per specifications with 20mm and down size aggregates with superplastisiser complete as per Drawing and Technical specifications i) upto 5m height | 167 | Cum | 8500 | 1419500
3 | (b) | Providing and laying in position reinforced cement concrete of design mix M30 as per specifications with 20mm and down size aggregates with superplastisiser complete as per Drawing and Technical specifications ii) For height upto 10 m | 269 | Cum | 8500 | 2286500
3 | (c) | Providing and laying in position reinforced cement concrete of design mix M30 as per specifications with 20mm and down size aggregates with superplastisiser complete as per Drawing and Technical specifications iii) For height above 10 m | 62 | Cum | 8800 | 545600
2 | 4.8 | Furnishing and Placing Reinforced cement concrete in super-structure as per drawing and Technical Specification complete as per specifications.RCC - with OPC cement design mix M30 as per specifications with 20mm and down size aggregates with superplastisiser complete as per Drawing and Technical specifications 10-15m | 634 | Cum | 9500 | 6023000
2 | 4.9 | Filling annular space around footing in rock with lean cement concrete 1:3:6 mix. | 3451 | Cum | 6500 | 22431500
2 | 4.10 | Reinforcement
3 | (a) | Supplying, fitting TMT bar reinforcement in sub-structure including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, tying with binding wire and anchoring to the adjoining members wherever necessary complete as per design, cost of materials, labour, HOM of machinery complete as per drawing and Technical specifications Fe 500 grade For foundation | 233 | MT | 68000 | 15844000
3 | (b) | Supplying, fitting TMT bar reinforcement in sub-structure including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design, cost of materials, labour, HOM of machinery complete as per drawing and Technical specifications Fe 500 grade For abutment, piers and pier heads | 71.5 | MT | 68000 | 4862000
3 | (c) | Supplying, fitting TMT bar reinforcement in super-structure including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design, cost of materials, labour, HOM of machinery complete as per drawing and Technical specifications Fe 500 grade For super-structure | 83 | MT | 70000 | 5810000
2 | 4.11 | Formwork
3 | (a) | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for foundation, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specifications | 982 | Sqm | 275 | 270050
| (b) | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. |  | Sqm
3 | (b) | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per speciications.
4 | (i) | 0-3.5m | 677 | Sqm | 425 | 287725
4 | (ii) | 3.5-4.5m | 284 | Sqm | 450 | 127800
4 | (iii) | 4.5-5.5m | 73 | Sqm | 475 | 34675
4 | (iv) | 5.5-6.5m | 73 | Sqm | 500 | 36500
4 | (v) | 6.5-7.5m | 73 | Sqm | 525 | 38325
4 | (vi) | 7.5-8.5m | 73 | Sqm | 550 | 40150
4 | (vii) | 8.5-9.5m | 73 | Sqm | 575 | 41975
4 | (viii) | 9.5-10.5m | 73 | Sqm | 600 | 43800
3 | (c) | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers lintels exceeding 1m in depth including cost of all materials, labour complete as per specifications 10.5-11.5m centering ht | 250 | Sqm | 600 | 150000
3 | (d) | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications 10.5-11.5m centering ht | 1743 | Sqm | 550 | 958650
3 | (e) | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for flat surface such as suspended floors, roofs, landing, balconies and likes, thickness, above 200 mm including cost of all materials, labour, complete as per specifications. 10.5-11.5m centering ht | 1087 | Sqm | 600 | 652200
2 | 4.12 | Painting
3 | (a) | Providing and finishing external walls in two coats with waterproof paint with primer of approved brand and shade to give an even shade after thoroughly brooming the surface to remove all dirt and loose powdered material free from mortar drops and other foreign matter cost of materials, labour complete as per specifications | 4982 | Sqm | 100 | 498200
3 | (b) | Painting the surfaces of thrust/anchor blocks above GL with cement paint as directed including lettering for identification of the blocks with approved paint. | 33 | Sqm | 85 | 2805
2 | 4.13 | Providing and laying cement concrete wearing coat with OPC cement design mix M30 as per specifications with 20mm and down size graded granite metal coarse aggregates and fine aggregates with superplastisiser including reinforcement complete as per drawing and specifications. | 87 | Cum | 12500 | 1087500
2 | 4.14 | Providing and fixing M.S. Hand railing for bridge super-structure with 50mm dia. M.S. hollow pipe of 14 gauge, welded to 20 mm x 20 mm M.S. square rod placed vertically, spaced at 100mm at regular intervals of 600mm. These vertical rods laterally tied to 3 horizontal rods spaced at equal interval. These assembly is fixed to concrete by using expansion bolts and welding the same to reinforcement bars and making good the surface. All the joints and sections should be cut to length, welded and grinded wherever necessary etc., complete. The work includes cost of all materials, labour charges for all items of work, hire charges for welding, cutting and grinding equipment, and elecricity charges, etc., complete as per specification and drawing | 722 | Sqm | 3000 | 2166000
2 | 4.15 | Supplying, fitting and fixing in position true to line and level elastomeric bearing conforming to IRC:83(Part-II) section IX and clause 2000.5 of MORTH Specifications complete including all accessories as per drawing and Technical Specifications complete as per specifications. MORTH Specification No. 2000 & 2200 | 207666 | C.C. | 1 | 207666
2 | 4.16 | Providing and laying of apron with cement concrete blocks of size 0.5x0.5x0.5 m cast in-situ and made with nominal mix of M-15 grade cement concrete with a minimum cement content of 240 kg / cum as pe IRC: 21-2000 complete as per specifications. | 290 | Cum | 6500 | 1885000
2 | 4.17 | Providing and laying of asphaltic plug joint to provide for horizontal movement of 25 mm and vertical movement of 2 mm, depth of joint varying from 75 mm to 100 mm, width varying from 500 mm to 750 mm (in traffic direction), covered with a closure plate of 200 mm x 6 mm of weldable structural steel conforming to IS: 2062, asphaltic plug to consist of polymer modified bitumen binder, carefully selected single size aggregate of 12.5 mm nominal size and a heat resistant foam caulking/backer rod, all as per approved drawings and specifications, complete as per specifications MORTH Specification No. 2600 | 108 | RM | 1400 | 151200
2 | 4.18 | Providing weep holes Brick masonry / Plain / Reinforcement concrete abutment, wing wall / return wall with 100mm dia AC pipe, extending through the full width of the structure with slope of 1V: 20H towards drawing force. Complete as per drawing and Technical Specifications complete as per specifications MORTH Specification No.2706 & 2200 | 224 | Nos | 200 | 44800
2 | 4.19 | Clearing and grubbing road land including uprooting rank vegetation, grass, bushes, shrubs, saplings and trees of girth upto 300mm, by manual means, in area of light jungle, removal of stumps, disposal of unserviceable materials, stacking of serviceable materials from road boundary, labour charges complete as per specifications. | 100 | Sqm | 7 | 700
2 | 4.20 | Loading and unloading of Stone Boulder / Stone aggregates / Sand / Kanker / Moorum, Placing tipper at loading point, loading with front end loader, dumping, turning for return trip, excluding time for haulage and return trip complete as per specifications. | 5659 | Cum | 85 | 481015
2 | 4.21 | Haulage of materials by tipper excluding cost of loading, unloading and stacking complete as per specifications for unsurfaced gravelled Road. | 50933 | t.km | 3 | 152799
2 | 4.22 | Providing and fixing M.S. ladder between landing 45 cms. Wide using angle iron of 65 x 65 x10 mm and 20mm M.S. bars at 25 cms. Centre to centre with necessary supports of same angle iron as directed including hand ariling on both sides with 25mm dia G.I. pipes with angle iron props at 2 mtrs, interval and 0.5 mtr, height including fixing in ground with C.C. 1:2:4 and two coats of non-poisonous anticorrosive bituminous paint with all lead and lift etc., complete as per specifications. | 10 | RM | 4000 | 40000
2 | 4.23 | Providing and laying boulders apron on river bed for protection against scour with stone boulders weighing not less than 40kg each complete as per drawing and technical specification complete as per specifications A.Boulder laid dry without wire crates | 1156 | cum | 3000 | 3468000
2 | 4.24 | Providing and laying filter material underneath pitching in slopes complete as per drawing and technical specification | 200 | cum | 1000 | 200000
2 | 4.25 | Diversion of water course by providing cofferdams or bunds or island as may be necessary for piers and abutments foundations, bailing out or pumping water during excavationand until completion beyond 1.5m depth upto & including 3m depth. | 1307 | cum | 3800 | 4966600
2 | 4.26 | Excavation of hard rock by diamond rope cutting method using machinery like generator(electric), hydraulic excavator,breaker,compressor and diamod rope with MS rods,etc.,complete as per specifications and directions of the Engineer in Charge. | 2415 | cum | 3000 | 7245000
WELL FOUNDATION
2 | 4.27 | Sinking of well from river bed level upto founding level through all strata as indicated in drawing including complete cost of setting out,sinking by dredging or any other approved method,use of kent ledge load as and when required,rectification in case of occurance of tilt and shift in well and all associated works involved with sinking of well.
3 | (a) | Upto 3m depth from surface | 39 | RM | 3000 | 117000
3 | (b) | Beyond 3m upto 6m from surface | 39 | RM | 3500 | 136500
3 | (c) | Beyond 6m upto 9m from surface | 39 | RM | 4000 | 156000
3 | (d) | Beyond 9m upto 12m from surface | 26 | RM | 4500 | 117000
2 | 4.28 | Providing and erecting formwork for the well curb, well steining and well cap to give F2 type of finish and removal of same. | 2600 | Sqm | 1000 | 2600000
2 | 4.29 | Providing and laying Reinforced Cement Concrete of grade M30 design mix as per specifications with coarse aggregates of size 20mm downgraded, including mixing, placing, vibrating, curing, etc complete but excluding cost of providing reinforcement and form work in :
3 | (a) | Well Curb | 72 | cum | 15000 | 1080000
3 | (b) | Well cap | 232 | cum | 16000 | 3712000
2 | 4.30 | Providing and laying Reinforced Cement Concrete of grade M30 design mix as per specifications with coarse aggregates of size 40mm downgraded, including mixing, placing, vibrating, curing, etc complete but excluding cost of providing reinforcement and form work in well steining. | 515 | cum | 13500 | 6952500
2 | 4.31 | Providing and laying M30 grade concrete design mix as per specifications in bottom plug of well by Tremie method with coarse aggregates of 20mm downgraded , with cement content being 10% more than the quantity required as per mix design to account for under water concreting including mixing, placing, vibrating, curing etc complete as per specifications. | 457 | cum | 14500 | 6626500
2 | 4.32 | Providing and laying plain cement concrete of 1:3:6 grade over the sand fill in the well foundation’s top plug with coarse aggregate of size 40mm downgraded including mixing, placing, compacting , curing etc complete as per specifications. | 46 | cum | 8200 | 377200
2 | 4.33 | Providing and filling of the well foundation with sand in layers of 225mm with proper ramming, which is free from organic matter, earth, clay, clod, roots, boulders and shingles including transportation, lifting , placing and compaction complete as per specifications. | 550 | cum | 1250 | 687500
2 | 4.34 | Supply, fabrication and erection of MS structural steel item in angle,plates etc. including necessary anchor bars for proper anchorage in concrete and painting of 2 coats of synthetic enamel paint over 2 coats of red oxide zinc chromate primer etc complete as per specifications. | 34 | MT | 215000 | 7310000
2 | 4.35 | Supply, fabrication and erection of the MS cutting edge for well curb as per details furnished in drawing and specific technical requirements including necessary check nuts or welding to keep the cutting edge well anchored in curb of well including painting, etc. complete as per specifications. | 26 | MT | 215000 | 5590000
RING GIRDER
2 | 4.36 | Providing, fabricating and fixing at site, anchor bolts including anchorage assembly, composed of plates, MS insert plates on RC saddles including cost of materials, labour, threads, nuts, lock nuts, washers, pipe sleeves, welding, etc. complete as per specifications and drawings. | 1 | MT | 215000 | 215000
2 | 4.37 | Supplying, fabricating, transporting and erecting ring girders at bridge piers and abutment locations on pipe shells including loading, unloading, welding with all necessary accessories etc., from steel plates / rolled sections conforming to IS : 2062 and as per specifications and drawings. | 46 | MT | 215000 | 9890000
2 | 4.38 | Supplying, fabricating, transporting and erecting of ring girder supporting structures including columns, base plates etc., from steel plates /rolled sections conforming to IS : 2062 including cutting, welding, grinding, machining, levelling etc as per specifications and drawings. | 17 | MT | 215000 | 3655000
2 | 4.39 | Providing, fabricating and transporting necessary holding down MS straps as shown in drawing or as directed including bolts, nuts and washers etc., complete as per specifications. | 2 | MT | 215000 | 430000
2 | 4.4 | Supplying, fabricating, delivering to site, loading, unloading, etc. and erecting structural steel work for strengthening of exisiting steel bridge including one shop coat of red oxide zinc chromate primer after fabrication and one coat of the same after erection and two coats of synthetic enamel paint of approved shade, etc. complete as per specifications. | 15 | MT | 215000 | 3225000
2 | 4.41 | Providing and fixing 100 mm dia - 10kg/cm2 PVC rain water pipes as per IS: 4984 including all fixtures such as brackets, bends etc.as directed by the Engineer. | 200 | RM | 1500 | 300000
| SUB TOTAL |  |  |  |  | 149287135
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 149287135

## V One Surge tank
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
BILL OF QUANTITIES - V : ONE WAY SURGE TANK
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
2 | 5.1 | Earth work excavation for foundation of structures by mechanical means in all types of soils exclusive of hard rock as per draiwng and technical specifications, including setting out,shoring,strutting,barricading,danger lighting,bracing,removal of stumps and other deleterious matter,dressing of sides and leveling of bottom of trenches to the extent required,etc. complete complete all as per specifications.
3 | (a) | 0 to 3 m depth | 3350 | Cum | 225 | 753750
2 | 5.2 | Earth work excavation for foundation of structures by mechanical means in hard rock as per drawing and technical specifications, including setting out,shoring,strutting,barricading,danger lighting,bracing,removal of stumps and other deleterious matter,dressing of sides and leveling of bottom of trenches to the extent required,etc. complete complete all as per specifications.
3 | (a) | 0 to 3 m depth | 1250 | Cum | 746 | 932500
2 | 5.3 | Backfilling around foundations of structures, etc.,with approved excavated soil including depositing in layers not exceeding 200 mm, watering, ramming manually and/or compaction with mechanical compaction machines to 95% Modified Proctor density,etc., complete all as specifictaions. | 1355 | Cum | 150 | 203250
2 | 5.4 | Disposing off the excess excavated earth of all types by vehicle including loading, unloading, with all leads,lifts, labour, HOM of machinery etc complete as per specifications. | 950 | Cum | 48 | 45600
2 | 5.5 | Providing and laying in position plain cement concrete of mix 1:3:6 with OPC cement content at 220Kgs using 40 mm and down size graded granite metal course aggregates @0.84cum and the fine agregates @0.56cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, in foundation and plinth for levelling course, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications. | 275 | Cum | 6782 | 1865050
2 | 5.6 | Providing and laying in position plain cement concrete of mix 1:2:4 with OPC cement content at 240Kgs using 20 mm and down size graded granite metal course aggregates @0.878cum and the fine agregates @0.459cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications. | 380 | Cum | 6500 | 2470000
2 | 5.7 | Providing and laying cement concrete in position reinforced cement concrete of design mix M30 as per specifications by pumping using 20 mm and down size granite Coarse aggregates & fine aggregates of ready mixed concrete (RMC) for R.C.C works laid in 15 cms thick layers and well compacted including vibrating, curing, including smooth finish in CM 1:3, with all lead and lifts etc., complete as per specifications. | 1187 | Cum. | 8500 | 10089500
2 | 5.8 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons. (Type F1 finish) | 1068 | Sqm | 300 | 320400
2 | 5.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for columns, pillars, piers, abutments, post and struts, square/rectangular/polygon in plan including cost of all materials, labour complete as per specifications. (Type F2 finish)
3 | (a) | Level from 0.00 to 3.50m | 350 | Sqm | 350 | 122500
3 | (b) | Level from 3.50 to 4.50m | 125 | Sqm | 350 | 43750
3 | (c) | Level from 4.50 to 5.50m | 100 | Sqm | 350 | 35000
3 | (d) | Level from 5.50 to 6.50m | 100 | Sqm | 350 | 35000
3 | (c) | Level from 6.50 to 7.50m | 100 | Sqm | 350 | 35000
3 | (d) | Level from 7.50 to 8.50m | 100 | Sqm | 350 | 35000
2 | 5.10 | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. (Type F2 finish)
3 | (a) | Level from 4.00 to 5.50m | 315 | Sqm | 450 | 141750
3 | (b) | Level from 5.50 to 6.50m | 245 | Sqm | 450 | 110250
3 | (c) | Level from 6.50 to 7.50m | 245 | Sqm | 450 | 110250
3 | (d) | Level from 7.50 to 8.50m | 245 | Sqm | 450 | 110250
2 | 5.11 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for sides and soffits of beams, beam haunchings, cantilever girders, bressumers and lintels not exceeding 1m in depth including cost of all materials, labour complete as per specifications. (Type F2 finish)
3 | (a) | Beams Level from 0.00 to 3.50m | 430 | Sqm | 300 | 129000
3 | (b) | Beams Level upto 4.50m | 430 | Sqm | 300 | 129000
3 | (c) | Beams Level upto 10m | 950 | Sqm | 300 | 285000
2 | 5.12 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs,etc. including cost of all materials, labours, complete as per specifications. | 1082 | Sqm | 650 | 703300
2 | 5.13 | Providing TMT steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design including cost of materials, labour, HOM of machinery complete as per specifications. Grade Fe 500 - CRS | 118 | MT | 68000 | 8024000
2 | 5.14 | Providing and laying 230 mm thick rubble packing in plinth with approved stone, set in regular lines, hand-packed, filling the interstices with approved small stone chips and sand, consolidating by ramming or compacting with heavy roller after watering, including spreading 12 mm layer of stone grit on top, etc., complete for all building works as per drawings, details and specifications. | 110 | Sqm | 500 | 55000
2 | 5.15 | Providing and constructing precast concrete solid blocks with compressive strength not less than 35kg. per sqm with cement mortar 1:4 masonry with solid concrete blocks of size 40x20x20 cms conforming to IS.2185/ 1965 in superstructure including cost of materials, labour charges, double scaffolding, curing complete as per specifications. | 300 | Sqm | 850 | 255000
2 | 5.16 | Providing plastering to masonry including providing and removing double scaffolding rounding of all corners whever required smooth rendering curing etc., complete as per specifications with burnt brick masonry plain plastering 20mm thick in CM 1:4 (external) | 280 | Sqm | 275 | 77000
2 | 5.17 | Providing plastering to masonry including providing and removing scaffolding rounding of all corners whever required, smooth rendering curing etc complete as per specifications with burnt brick masonry plain plastering 12mm thick in CM 1:4 with lime rendering (internal) | 300 | Sqm | 225 | 67500
2 | 5.18 | Providing and finishing external walls in two coats with waterproof cement paint of approved brand and shade to give an even shade after throughly brooming the surface to remove all dirt and loose powdered material, free from mortar drops and other foreign matter cost of materials, labour, complete as per specifications. | 2536 | Sqm | 100 | 253600
2 | 5.19 | Providing and applying painting in two coats with plastic emulsion paint of approved brand on wall surface to give an even approved shade after thoroughly brushing the surface, free from mortor drops and other foreign matter including preparing the surface even and sand paper smooth, cost of materials, labour, complete as per specifications. | 410 | Sqm | 100 | 41000
2 | 5.2 | Providing and laying flooring and steps fine machined polished granite stone slabs of approved colour 20mm thick on cement mortar bed 1:6, 20mm thick, and, joints finished with cement mortar 1:3 over existing cement concrete bed ,including cost of materials, labour, curing complete as per specifications. | 90 | Sqm | 1500 | 135000
2 | 5.21 | Providing and fixing skirting of 300mm high using prepolished water cut/gang saw of 19mm thick grey granite 0.5mm wide chamfered width and depth and fixing in CM 1:4 of 20mm thick after chipping the walls, etc., including cost of all materials, mortar,labour,curing,etc., complete as per specifications. | 25 | Sqm | 9500 | 237500
2 | 5.22 | Providing dado, treads, rises of steps with colour glazed tiles on 10mm thick cement plaster 1:3 and jointed with white cement slurry over rough plaster surface using glazed tiles of approved make and size including flush pointing of joints with white cement added with pigments to match colour of tiles, curing cost of materials, labour, complete as per specifications. | 40 | Sqm | 3800 | 152000
2 | 5.23 | Providing and laying M-15 cement concrete flooring, 60mm thick with metallic concrete hardner topping, under layer of 45mm thick M-15 cement concrete using broken granite metal of 20mm and downsize and top layer of 15mm thick metallic cement hardner consisting of mix 1:2 by volume, with metallic hardening compound of approved quality mix in the ratio of 4:1, including finishing, cost of materials, labour, curing, complete as per specifications. | 125 | Sqm | 1500 | 187500
2 | 5.24 | Providing and fixing ceramic tiles (non skid) of size 400x400mm for flooring laid on a bed of 20mm thick cement mortar 1:3 mix flush pointing with white cement mixed with matching colour pigment including curing, cleaning,etc., complete.The work includes cost of all materials,mortar,labour charges for all items of work,hire charges for equipment,etc., complete as per specifications. | 50 | Sqm | 3000 | 150000
2 | 5.25 | Providing and fixing mortice door lock as per IS : 2209 of approved make and design. | 4 | No. | 1400 | 5600
2 | 5.26 | Providing and fixing mechanical gear type rolling shutters of approved make out of 18 guage, 75mm wide cold rolled steel laths of convex corrugation, with side guides and bottom rail, with interlocking arrangements for steel laths by means of alternate clips, suspension shaft with High tension coil type springs two numbers, mounted on specially designed pipe shaft, with bracket plates, guide channels, ball bearing arrangements, for inside & outside locking with push & pull operations complete including pulling hooks, 4nos. handles with all fittings and accessories, painted with a coat of red lead paint (without top cover) cost of materials, labour, HOM of machinery complete as per specifications. | 21 | Sqm | 15000 | 315000
2 | 5.27 | Providing and fixing 150 mm diameter cast iron air ventilators as per design & shape indicated in drawings over roof slab of all reservoirs with mosquito proof jali etc complete. | 16 | No. | 2500 | 40000
2 | 5.28 | Providing and fixing 225 mm wide and minimum 6 mm thick continuous PVC waterstops of approved quality at contraction and expansion joints as per manufacturer's instructions at all levels complete as per specifications. | 111 | RM | 450 | 49950
2 | 5.29 | Providing and fixing white vitreous china clay, water closet European type (Pedestal type, P-trap) with black solid plastic seat and lid, CP brass hinges, rubber buffers, 10 litre low level, P.V.C flushing cistern (all are approved make) with fittings, SS brackets, 40mm diameter flush bend with fittings and clamps, overflow arrangements with specials and 25mm mosquito proof coupling of approved design, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 1 | No. | 4000 | 4000
2 | 5.3 | Providing and fixing white vitreous china clay, flat back wash basins of size 550 mm x 400 mm with a pair of 15mm C.P brass pillar taps with SS brackets, 32mm C.P brass waste of standard pattern, painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 1 | No. | 4500 | 4500
2 | 5.31 | Providing and fixing white vitreous china clay, flat back, lipped front urinal basin of 430x260x350mm in the range of three with 7.5 litres PVC automatic flushing cistern, SS brackets, standard flush pipe and C.P brass spreaders with brass unions and G.I clamps painting of fittings and brackets, cutting and making good the wall and floor wherever required, including cost of materials, labour complete as per specifications. | 2 | No. | 6500 | 13000
2 | 5.32 | Providing and fixing in position brass bib cock of aproved quality 15mm nominal bore including cost of all materials, labour and HOM of equipments with all leads complete as per specifications. | 2 | No. | 525 | 1050
2 | 5.33 | Providing brick masonry inspection chambers, rectangular in size 90 cm x 45 cm and upto 1.5 m depth, with 230 mm brick wall in cement mortar (1:2), plastered both inside and outside with 20 mm thick cement mortar (1:2),including cement concrete 1:2:4 top slab and bottom foundation slab as per standard plan including excavation, backfilling the excavated sides and removing surplus earth and with heavy duty C.I. cover and frame and with M.S. steps fixed in cement mortar with cement and sand filleting. | 1 | No. | 10500 | 10500
2 | 5.34 | Providing and fixing PVC Nahani trap of approved make conforming to ISI specifications and construction of cistern in M-15 as per directions. (rate inclusive of cost of materials and fixtures and conveyance of materials to work spot). | 4 | No. | 350 | 1400
2 | 5.35 | Providing stoneware gully trap of approved quality and make fixing in M-15 and plastering with CM 1:3 wherever necessary. (rate includes cost of all materials, fixtures and lead). With 100mm outlet. | 1 | No. | 225 | 225
2 | 5.36 | Providing and fixing white glazed 'P' trap as per IS 2556 (Part 7) 100 mm dia with C.I. grating 10 mm thick etc., complete. | 1 | No. | 125 | 125
2 | 5.37 | Providing and fixing cast copper alloy stop valves, polished bright, conforming to and as per IS 781.
3 | (a) | 25 mm dia. | 1 | No. | 195 | 195
3 | (b) | 20 mm dia. | 1 | No. | 185 | 185
3 | (c) | 15 mm dia. | 1 | No. | 180 | 180
2 | 5.38 | Installing precast circular hume pipe septic tank and constructing standard soak pit, suitable for 10 persons capacity, piping of stoneware including excavation and backfilling of pit, stoneware piping, filling soakpit with broken bricks, overflow connection precast RC slab and construction of manhole chamber with cover, C.I. vent pipe with cowl and connecting it to incoming and outgoing pipelines etc., complete. | 1 | No. | 25000 | 25000
2 | 5.39 | Providing and fixing SS towel rail 740mm length, 20mm dia with C.P brackets, fixed to wooden cleats with C.P brass screws including cost of materials, labour complete as per specifications. | 1 | No. | 1000 | 1000
2 | 5.4 | Providing and fixing best quality SS liquid soap bottle holders of approved make with SS brackets, screws, rawl plugs, etc. complete. | 1 | No. | 1000 | 1000
2 | 5.41 | Providing and fixing 600x450 bevellead edge mirror of superior glass with 6mm hard board backing and fixed to wooden cleats with C.P screws, washers, including cost of materials, labour complete as per specifications. | 1 | No. | 1500 | 1500
2 | 5.42 | Providing and fixing UPVC water pipes, pressure rating of 10 kg/cm2 with all necessary fixtures and bends, including testing the line as specified etc. complete as per specifications.
3 | (a) | 25 mm dia. | 100 | RM | 250 | 25000
3 | (b) | 20 mm dia. | 50 | RM | 175 | 8750
3 | (c) | 15 mm dia. | 25 | RM | 125 | 3125
2 | 5.43 | Providing and Fixing PVC soil waste and vent pipes 100 mm diameter - 10kg/cm2 with spun yarn soaked in cement slurry and cement mortar 1:2 including cost of materials, labour, testing complete as per specifications. | 200 | RM | 175 | 35000
2 | 5.44 | Providing and fixing PVC pipes of approved make and 150 mm dia - 10kg/cm2 conforming to IS 651, including all necessary fixtures and bends, including excavation, backfilling, testing etc., complete as per specification. | 200 | RM | 250 | 50000
2 | 5.45 | Providing and fixing 100 mm dia - 10kg/cm2 PVC rain water pipes as per IS: 4984 including all fixtures such as brackets, bends etc.as directed by the Engineer. | 100 | RM | 275 | 27500
2 | 5.46 | Providing and fixing cast iron bell mouth rain water outlets including MS grating, etc., complete as directed by Engineer. | 10 | No. | 1400 | 14000
2 | 5.47 | Providing and fixing M.S. ladder between landing 45 cms. Wide using angle iron of 65 x 65 x10 mm and 20mm M.S. bars at 25 cms. Centre to centre with necessary supports of same angle iron as directed including hand ariling on both sides with 25mm dia G.I. pipes with angle iron props at 2 mtrs, interval and 0.5 mtr, height including fixing in ground with C.C. 1:2:4 and two coats of non-poisonous anticorrosive bituminous paint with all lead and lift etc., complete as per specifications. | 10 | RM | 4000 | 40000
2 | 5.48 | Providing and fixing 304- grade Stainless steel handrails of 14 gauge pipe for ramps or staircase are made out of stainless steel hollow pipes, using 50mm dia for verticals @ 1.60mtr c/c are fixed to the rams or steps by drilling with bolts and 100mm dia MS base plates 10mm gauge for fixing of vertical pipes 4 nos anchor bolts & 40mm dia pipes are fixed horizontally for 2 rows top one pipe are fixed with vertical pipes another one are fixed with elbows & 25mm dia pipes are fixed horizontally for 2 rows with elbow top measure @ equal intervals including cutting, welding, bending wherever necessary with suitable caps @ tops, bottoms, corners finishing with mat/shining etc., completeincluding cost and conveyance of all materials, labour for all items of work, HOM of euipment with all lead and lift, loading and unloading, transportation charges and all other incidental charges etc., complete as per specification and directions of the Engineer-in-charge of the work. | 171 | RM | 3200 | 547200
2 | 5.49 | Providing, fabricating, assembling and fixing in position anodized aluminium doors using following alluminium mat finish or glossy finish, outer frame plain section 101.6x44.45mm thickness 3.18mm, section weight 2.404kg/m, door shutters vertical section 44.62x44.45mm thickness 3.18mm, section weight 1.505kg/m, top section 47.62x44.45mm thickness 3.00mm, section weight 1.426kg/m bottom section 114.3x44.45thickness 3.18mm section weight 2.646kg/m, door central section 49.91x44.45mm thickness 3.00mm, section weight 1.495kg/m glazing clips 19x17.3x11mm thickness 0.9mm section weight 0.124kg/m; aluminium sections anodized 12 to 15 microns cut to length joint metred corners grinded, the shutters pivoted opening arrangement with heavy duty aluminium alloy automatic door closures floor mounted, providing and fixing standard approved accessories, such as aluminium handle for full width or length, tower bolts, lock, pivots; P.V.C. or rubber gasket with 5.5m thick plain glass for top and bottom panel; aluminium sections treated for removal of any rust and prevention of further rust formation, and coated with greasy materials for non-adherance of mortars or any other sticky materials; the assembled frame fitted with the corner angles, strips and fitted with screws, rawl plugs or teakwood gutties to R.C.C. columns or masonry on sides, beams and flooring in bottom, including cutting, chistling and making good with cement mortar to match the surface; all the frames throughly cleaned free from rust, scale, or dirt including cost of materials, fixtures, labour and HOM of machinery, complete as per specifications - aluminium section anodised to 12-15 microns. | 11 | Sqm | 7500 | 82500
2 | 5.5 | Providing and fixing in position anodized aluminium windows and ventilators as per approved drawings with sliding shutters using double track window frame section of size 61.85x31.75mm. with 1.2mm thick, bottom section weight 0.695 kg/m; sides and top sections 1.3 mm. thick weight 0.659 kg/m; and shutter comprising top and bottom section of size 40mmx18mm, 1.25mm thick 0.417 kg/m; shutter outer side 40mmx18mm, 12.5mm, thick weight 0.417 kg/m, shutter interlock section 40mmx26.7mm, 1.1mm thick, weight 0.469 kg/m. the shutters mounted on nylon rollers with approved quality of fixtures such as aluminium handles tower bolts etc., and providing and fixing 5.5mm, thick plain glass for shutters fitted with rubber beading aluminium sections anodised 12 to 15 microns, including cutting to required length, joints mitred subdividing the frame tenonned and rivetted in the assembled frame stiffened with end clips at corners angles etc., and fixed to the walls, lintels, floor beams/cills as the case may be with necessary steel screws, raul plugs, or teak wood gatties including cutting masonry or concrete and making good the original surface using cement mortar, aluminium sections pretreated for removal of any Specification (aluminium section anodised to 12-15 microns) | 14 | Sqm | 5000 | 70000
2 | 5.51 | Supplying and fixing PVC encapsulated CI rungs to shapes and at locations specified in drawings and complete as per specifications. | 50 | kg | 150 | 7500
2 | 5.52 | Providing and fixing hydraulic door closures -Aluminium body | 6 | No. | 3000 | 18000
2 | 5.53 | Supplying of and application of food grade epoxy painting on the inside surface tank complete, as per applicable Technical specification clause, including all labour, HOM of equipment, lead, lifts taxes etc., complete, including all surface preparation, testing, Rate shall be inclusive of all materials, tools and plants, testing and inspection etc., complete. | 380 | Sqm | 775 | 294500
2 | 5.54 | Providing and filling polysulphide rubberised sealing compound or equivalent at the joints including forming groove as specified on drawing complete as per specifications. | 111 | RM | 2000 | 222000
2 | 5.55 | Providing and laying in position yelahanka tiles of size 125 x 250mm of approved quality and make, over a bed of cement mortar 1:3 with thickness varying from 100mm to 25mm including weather proof course and pointed with cement mortar 1:3 mix with red oxide including curing cost of materials, labour complete as per specifications | 500 | sqm | 3800 | 1900000
2 | 5.56 | Supplying, fabricating, delivering to site, loading, unloading, etc. and erecting structural steel work including one shop coat of red oxide zinc chromate primer after fabrication and one coat of the same after erection and two coats of synthetic enamel paint of approved shade, etc. complete as per specifications. | 2 | MT | 215000 | 430000
2 | 5.57 | Providing and fixing MS frame with 10 mm thick flat grating cover with stiffeners for openings as specified in drawing at all locations and levels, including painting, etc., complete. | 1000 | kg | 160 | 160000
| SUB TOTAL |  |  |  |  | 32749685
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 32749685

## VI.NH Crossings
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
BILL OF QUANTITIES - VI : NH CROSSINGS
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
2 | 6.1 | Earthwork excavation for pipeline trenches and foundations of structures, etc. in all types of soils exclusive of hard rock, by mechanical / & manual means including dressing sides,ramming of bottoms, providing barricading,shoring,strutting,dewatering,etc. complete all as per specifications.
3 | (a) | 0 to 2 m depth | 5700 | Cum | 175 | 997500
3 | (b) | 2 to 4 m depth | 5700 | Cum | 250 | 1425000
3 | (c) | 4 to 6 m depth | 3000 | Cum | 325 | 975000
3 | (d) | > 6 m depth | 1800 | Cum | 375 | 675000
2 | 6.2 | Earth work excavation for pipeline trenches and foundations of structures,etc in hard rock by mechanical / & manual means including dressing sides, ramming of bottoms, providing barricading,danger lighting shoring, strutting, dewatering,etc. complete all as per specifications.
3 | (a) | 0 to 2 m depth | 1500 | Cum | 1700 | 2550000
3 | (b) | 2 to 4 m depth | 1500 | Cum | 1800 | 2700000
3 | (c) | 4 to 6 m depth | 1500 | Cum | 1900 | 2850000
3 | (d) | > 6 m depth | 600 | Cum | 2000 | 1200000
2 | 6.3 | Backfilling around pipeline trenches and foundations of structures, etc.,with approved excavated soil including depositing in layers not exceeding 200 mm, watering, ramming manually and/or compaction with mechanical compaction machines to 95% Modified Proctor density,etc., complete all as per specifictaions. | 6900 | Cum | 115 | 793500
2 | 6.4 | Disposing off the excess excavated earth of all types by vehicle including loading, unloading, with all leads,lifts, labour, HOM of machinery etc complete all as per specifications | 9300 | Cum | 48 | 446400
2 | 6.5 | Providing and laying in position plain cement concrete of mix 1:2:4 with OPC cement content at 240Kgs using 20 mm and down size graded granite metal course aggregates @0.878cum and the fine agregates @0.459cum machine mixed, concrete laid in layers not exceeding 15 cms. thick, well compacted, including cost of all materials, labour, HOM of machinery, shuttering, curing complete as per specifications. | 600 | Cum | 6500 | 3900000
2 | 6.6 | Providing and laying cement concrete in position reinforced cement concrete of design mix M30 as per specifications by pumping using 20 mm and down size granite Coarse aggregates & fine aggregates of ready mixed concrete (RMC) for R.C.C works laid in 15 cms thick layers and well compacted including vibrating, curing, including smooth finish in CM 1:3, with all lead and lifts etc., complete as per specifications. | 4200 | Cum. | 7000 | 29400000
2 | 6.7 | Providing and removing centering, shuttering, strutting, propping etc., and removal of form work for foundations, footings, bases of columns for mass concrete including cost of all materials, labour complete as per specificaitons. (Type F1 finish) | 3600 | Sqm | 450 | 1620000
2 | 6.8 | Providing and removing centering, shuttering, strutting, propping etc. and removal of form work for vertical surface such as walls at any thickness, including attached pilasters, buttesses, plinth and string courses cost of all materials, labour complete as per specifications. (Type F2 finish) | 7800 | Sqm | 450 | 3510000
2 | 6.9 | Providing and removing centering, shuttering, strutting, propping etc and removal of form work for flat surface such as suspended floors, roofs,etc. including cost of all materials, labours, complete as per specifications. | 2100 | Sqm | 450 | 945000
2 | 6.10 | Providing TMT steel reinforcement for R.C.C. work including straightening, cutting, bending, hooking, placing in position, lapping and / or welding wherever required, trying with binding wire and anchoring to the adjoining members wherever necessary complete as per design including cost of materials, labour, HOM of machinery complete as per specifications. Fe 500 grade | 600 | MT | 68000 | 40800000
2 | 6.11 | Construction of Granular sub-base by providing coarse graded material, spreading in uniform layers on prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density, complete for Grading-iii as per MORTH Specifications. | 750 | Cum | 3500 | 2625000
2 | 6.12 | Providing, laying, spreading and compacting graded stone aggregate to Wet Mix Macadam (WMM) specification including premixing the material with water at OMC in mechanical mix plant carriage of mixed material by tipper to site, laying in uniform layers in sub base/ base course on well prepared surface and compacting with vibratory roller/ tamper/plate vibrator to achive the desired density complete as per specifications. | 540 | Cum | 4000 | 2160000
2 | 6.13 | Providing and applying Primer Coat with bitumen emulsion using emulsion pressure distributor at the rate of 0.60 kg per sqm on the prepared WMM surface including cleaning of WMM surface and spraying primer using mechanical spray jet as per MORTH specification clause No. 502 complete as per specifications. | 3300 | Sqm | 90 | 297000
2 | 6.14 | Providing and applying Tack Coat on the prepared WMM surface hot bitumen primed at 1kg per sqm heating bitumen in boiler fitted with spray set including cost of all materials,labour,etc as per MORTH specification complete as per specifications. | 3300 | Sqm | 45 | 148500
2 | 6.15 | Providing and laying Bituminous Macadam using 100-120TPH hot mix plant using crushed aggregates of specified grading premixed with bituminous binder, transported to site, laid over a previously prepared surface to the required grade, level and alignment and rolled by virbratory roller as per MORTH specification to achieve the desired compaction complete with all lead and lift and direction of Engineer-in-charge. | 247.5 | Cum | 12000 | 2970000
2 | 6.16 | Providing and applying Tack Coat on the prepared BM surface at 0.5kg per sqm heating bitumen in boiler fitted with spray set as per MORTH specification complete as per specifications. | 5400 | Sqm | 45 | 243000
2 | 6.17 | Providing and laying Semi Dense Bituminous Concrete(SDBM) using 100-120 TPH hot mix plant using crushed aggregates of specified grading, premixed with bituminous binder 5.4 to 5.6 per cent of mix and filler, transporting the hot mix to work site, laying with a hydrostatic paver finisher with mechanical control to the required grade, level and alignment, rolling with smooth wheeled, vibratory and tandem rollers to achieve the desired compaction as per MORTH specification complete with all lead and lift, with 60/70 Grade bitumen and direction of Engineer-in-charge. | 1890 | Cum | 15000 | 28350000
2 | 6.18 | Construction of RCC railing of M30 Grade design mix in-situ with 20mm nominal size aggregate, true to line and grade,tolerance of vertical RCC post not to exceed 1 in 500,centre to centre spacing between vertical post not to exceed 2000mm,leaving adequate space between vertical post for expansion,complete as per approved drawings and MORTH specifications complete as per specifications. | 180 | RM | 12500 | 2250000
| SUB TOTAL |  |  |  |  | 133830900
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 133830900

## VII-Electrical
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
BILL OF QUANTITIES - VII : ELECTRICAL WORKS
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
LT Electrical Works for Surge Tank at JK Doddi
2 | 7.1 | Supply, Installation & Commissioning of 63Amps Three Phase 500V 4 Pole Change Over Switch erected on iron angle/frame with approved make | 1 | No. | 16500 | 16500
2 | 7.2 | Supply, Transportation, loading/unloading, Laying, Installation & Commissioning of Solid Aluminum conductor up to 10 sqmm balance stranded conductor, XLPE Insulated, cores laid up, PVC tape/Extruded Innersheathed for Multicore Cables , Armour (Aluminium wire for single core up to 70 sqmm balance Aluminium strip, Glavanised wire for cables upto 2x10 sqmm, 3x10 sqmm,4x6 sqmm balance all galvanised steel strip), extruded PVC Type ST2 sheathed, 650/1100V grade as per IS 7098(Part 1) 1988, Incoming Cable from nearst 415V and as per single line diagram ONTB/BWSSP(III)/CP-07/EL/1040
3 | (a) | 3.5C x 25sq.mm (Al. Conductor) | 200 | Mtr | 550 | 110000
3 | (b) | 3.5C x 25sq.mm (Al. Conductor) - Glands | 6 | No. | 300 | 1800
3 | (c) | 3.5C x 25sq.mm (Al. Conductor) - Lugs | 24 | No. | 50 | 1200
2 | 7.3 | 415V Panel Board: Supply, Transportation, Installation, Testing & Commissioning of 415V LT Board of cubicle type with 415V, 50 Hz, 3 PH, TPN, 25 kA for 1 sec, wtih IP-54 enclosure with Bottom entry, consisting of incoming and outgoing feeders with metering and protection with complete accessories as per specification and single line diagram ONTB/BWSSP(III)/CP-07/EL/1040.
3 | (a) | Incomer: 63A, 25kA, 4P, MCCB | 1 | No. | 20000 | 20000
3 | (b) | CT Ratio-75/5A, Class-1 accuracy, 5 VA | 3 | No. | 1600 | 4800
3 | (c) | LED Indication Lamps for Red & Yellow Indication with 6A SP MCB for Protection of each lamp | 2 | No. | 300 | 600
3 | (d) | LED Indication Lamps for Blue Indication with 6A SP MCB for Protection of each lamp | 1 | No. | 300 | 300
3 | (e) | LED Indication Lamps for ON/OFF/Trip indications | 29 | No. | 300 | 8700
3 | (f) | Supplying & Erecting 100A rated 3 Phase with neutral bus bar using required capacity electrolytic copper strips covered with heat shrikkable coloured PVC sleeve, mounted on Phenolic/FRP/DMC insulator which are mounted on powder coated 40x6 mm MS flat frame work in existing panel board. The bus bar shall have suitable holes for termination of incoming and outgoing cables as per IS specification with necessary bolts, nuts and washers etc. complete.TPN copper Bus bar Chamber with Heat shrink sleeves for Phases & Neutral. | 5 | Mtr | 5000 | 25000
3 | (g) | Outgoing: 32A 4P MCB (Indoor Lighting DB) | 1 | No. | 7000 | 7000
3 | (h) | Outgoing: 6-10A TPN MPCB (Butterfly Valve Actuator and Spare) | 7 | No. | 2500 | 17500
3 | (i) | Outgoing: 32A TPN MCB (Street Lighting, UPS with SCADA Panel and spare) | 5 | No. | 4500 | 22500
3 | (j) | Single phase Digital Ammeter | 7 | No. | 5000 | 35000
3 | (k) | LT Three Phase, 4wire, CT operated multifunction meter, V, I, kW, F, Pf, kVA, kVAR, Phase angle class 1 accuracy with RS 485 communication | 1 | No. | 40500 | 40500
3 | (l) | DOL Starter, contactor with Pushbutton and Pushbutton station station, no volt coil, O/L release and required power & control wiring complete | 7 | No. | 6500 | 45500
3 | (m) | Panel Fabrication with enclosures, earthing bus, wiring, control relays, Auxiliary contactors, Control Transformers, power contactors, Control MCBs, terminal blocks etc. All complete works.
2 | 7.4 | Indoor Lighting DB: Supply, Transportation,Installation, testing & Commissioning of 4 Way TPN DB Horizontal with IP 43 Protection as per IS:13032 and suitable for 12 Nos D.P. out goings and for 1 No 4 pole Incomer with IP-54 enclosure, bottom entry cable, necessary accessories like wiring, contactors, terminal block, aux. relays, timer etc complete and as per single line diagram ONTB/BWSSP(III)/CP-07/EL/1040
3 | (a) | Incomer: 32A, 4P, MCB | 1 | No. | 6500 | 6500
3 | (b) | Incomer: 100 mA 4 Pole RCCB | 1 | No. | 25000 | 25000
3 | (c) | LED Indication Lamps for Red & Yellow Indication, with 6A SP MCB for Protection of each lamp | 2 | No. | 300 | 600
3 | (d) | LED Indication Lamps for Blue Indication with 6A SP MCB for Protection of each lamp | 1 | No. | 300 | 300
3 | (e) | Outgoings: 16A, DP, MCB | 12 | No. | 700 | 8400
3 | (f) | Outgoings: 30mA, 2 Pole RCCB | 6 | No. | 3500 | 21000
3 | (g) | LED Indication Lamps for ON/OFF indications | 2 | No. | 300 | 600
3 | (h) | Panel Fabrication with enclosures, earthing bus, wiring, control relays, Auxiliary contactors, Control Transformers, power contactors, Control MCBs, terminal blocks etc. All complete works.
2 | 7.5 | LT Cables
3 | (a) | Supplying, Erection & Termination of XLPE armoured cable copper conductor continuous 5.48 sq.mm. (12 SWG) GI earth wire complete erected with glands & lugs, on wall/trusses/pole or laid in provided trench/pipe as per specifications.
4 | i) | 4Cx6 sq.mm | 150 | Mtr | 400 | 60000
4 | ii) | 3Cx4 sq.mm | 200 | Mtr | 300 | 60000
3 | (b) | PVC insulated, sheathed flexible copper cable
4 | i) | 2Cx4 sq.mm | 100 | Mtr | 250 | 25000
3 | (c) | Brass Cable Glands Supply & termination with all related accessories complete
4 | i) | 4Cx6 sq.mm | 6 | No. | 200 | 1200
4 | ii) | 3Cx4 sq.mm | 12 | No. | 200 | 2400
3 | (d) | Brass Cable Lugs Supply & termination with all related accessories complete
4 | i) | 4Cx6 sq.mm | 24 | No. | 10 | 240
4 | ii) | 3Cx4 sq.mm | 36 | No. | 8 | 288
2 | 7.6 | Lighting System :
3 | (a) | Supply, installation, testing & commissioning of Light Luminares complete with: a) All accessories including mounting for fully functioning of fixture (Indoor & Outdoor). b) Earthing of fittings. c) Lamp of suitable wattage.
4 | i) | 40W LED Batten luminaire suitable for Surface Mounting/ Suspended mounting. (Indoor Areas) | 6 | No. | 3800 | 22800
4 | ii) | Emergency Lighting: Supply & Fixing of Rechargeable emergency lamp (600 mm fluorescent lamp) or LED lamp with accessories complete | 1 | No. | 7000 | 7000
3 | (b) | Fixing of Fittings
4 | i) | Fixing all types & all capacities fluorescent/ CFL fittings Indoor on the wall /ceiling/rafters/gridders using 23 / 0.76 " twin twisted PVC insulated wires. | 6 | No. | 600 | 3600
3 | (c) | Supply, Installation & commissioning of LED Street light Luminaire made of pressure diecast alluminium body with powder coated, having protective toughned glass, Supply Input voltage 120 - 270 V AC, P.F > 0.90, high power LED's having System efficacy > 95 lm/W and junction temprature < 70°C, with Ingrees protection IP65, Luminaire performance complies to IS 10322 (Part 5 / Sec-3), Driver surge protection 4KV, external Surge protection ≥ 5KV with optics distribution , THD<10% at 110 Volts AC, driver efficiency >90%, CCT: 3000K - 5700K, minimum CRI>70, etc., complete a) LUMINAIRE MAKE : WIPRO / PHILIPS (GREEN LINE) / Lighting Technologies(Adornis) / SCHREDER (BRIKA) / GE / VIN (MATRIX) / CROMPTON (HAWK) / BAJAJ (EDGE+) / HALONIX (LUMOS - SUPER) / HAVELLS (ENDURA CITYLINER NEO) b) LED MAKE : PHILIPS
4 | i) | 60W | 4 | No. | 10500 | 42000
3 | (d) | LED Driver Supply, Installation, testing & Commissioning of Following equipment with necessary items with complete
4 | i) | LED Driver as per IS 15885 (Part 2 / Sec 13)..2012 with input line voltage 120V-270V AC, 50Hz with surge protection of 4.0 KV, IP20, suitable for 45-90W, LED street light fitting with 2 Years Warranty. | 4 | No. | 10500 | 42000
3 | (e) | Supply & Erection of 40mm dia. GI Pipe bracket up to 2.7 mtrs long for fixing MV/SV/MH/FTL street light fitting of all capacities on rail/RCC/Wall/tubular pole, using suitable clamps, bolts, nuts and wiring etc complete. | 4 | No. | 30000 | 120000
3 | (f) | Fabrication, Transportation and erection of hot-dip galvanized Octogonal Pole with BSEN - 10025 grade S 355 JO steel plate for shaft, IS 2062 for base plate with door opening arrangement, including the supply of suitable boards with bakelite sheet as per IS specification suitable to withstand the wind speed of 180 KMPH for 7.5 Mtrs height Pole having dimensions Bottom 130 mm,. Top 70mm with 3mm thick, base plate 220 x 220 x 12mm and 4 Nos of M20 x 700 long 'J' bolts along with template. | 4 | No. | 30000 | 120000
3 | (g) | Foundation and erection charges with special T&P, for 7.50 Mtrs long Octagonal /Conical pole duly erecting on base plate duly providing 4 Nos foundation bolts with nuts with providing of 0.45Mtr x 0.45Mtrs x1.20 Mtr size M20 cc work vibrated concreting mixing with necessary steel (10kgs) reinforcement and curing for 7 days as directed by the field engineers during execution including excavation of Earth/BT all labour charges and cost and conveyance of materials etc.complete. | 4 | No. | 6500 | 26000
3 | (h) | Fabrication, Transportation and erection of 1.0 Mtr Length Bracket or any decorative single arm with dooms either sides complete with all accessories with MS galvanised 40/50mm dia pipe | 4 | No. | 3000 | 12000
3 | (i) | Supply & Erecting of thermo plastic Pole mounted cable junction box/cut-out box/fusebox for road/street lighting for 3 phase/4 core cables with IP 65 protection and metric knockouts for cable entry including threaded cable gland suitable for industrial applications.​ | 4 | No. | 3000 | 12000
3 | (j) | Earthing (for Street Light):
4 | i) | Supply & Erecting of GI grounding pipe, B-class, 42mm dia, 2.5mtrs long, 3.2mm thick with bolts nuts, GI strips and washers complete (earthing pits) Min. weight of the GI pipe:7.3Kgs. | 4 | No. | 12500 | 50000
4 | ii) | Good quality well burnt charcoal for grounding purposes packed in non returnable gunny bags of 30Kg each | 4 | No. | 2500 | 10000
4 | iii) | Good quality Salt for grounding purposes packed in 50Kg gunny bag | 4 | No. | 2500 | 10000
2 | 7.7 | Supply & Erection of Plug, Sockets, Switches with accessories and enclosure
3 | (a) | 240V, 3pin, 1Ph, & N, 5A socket-Industrial Type | 3 | No. | 8500 | 25500
3 | (b) | 240V, 3pin, 1Ph, & N, 15A socket-Industrial Type | 3 | No. | 10500 | 31500
3 | (c) | Surface / flush mounting 4-5 way unbreakable PVC modular box suitable for mounting modular switch plates.The box should be firmly/surface/flush mounted after due groove cutting in brick / cc wall, fixing including necessary rawl plugs, Machine/NF screws etc. | 3 | No. | 250 | 750
3 | (d) | 4 module modular switch mounting polycorbonate plate with necessary supporting back plate with required nos. of machine screwws, bolts nuts etc., complete on the existing metal / PVC box. | 3 | No. | 250 | 750
2 | 7.8 | Earthing
3 | (a) | Supplying, fixing and wiring earth electrode for grounding conduits, I.C.cutouts and other equipments on the meter board using 40 mm dia 2.9 thick GI pipe 2.5 meter long buried in a pit. The pit should be filled with equal proportion of salt charcoal 150mm alround the pipe to complete depth. The connection from the pipe to the conduit etc, is to be established through GI wire of size as per ISI specification 7.3.3 of IS 732 using 12mm dia bolts, nuts washers and check nuts etc, the pipe shall have 16 through holes of 12.2mm dia. (treated earth pits) | 2 | No. | 12500 | 25000
3 | (b) | 40x6 mm GI Earth Strip | 50 | Mtr | 300 | 15000
3 | (c) | 25x3 mm GI Earth Strip | 120 | Mtr | 200 | 24000
3 | (d) | 8 SWG GS Wire | 150 | Mtr | 1000 | 150000
2 | 7.9 | Lightning Protection System Supply, Erection & Commissioning of Lightning Protection equipment with accessories and fixing arrangement etc. complete
3 | (a) | Supply & installation of Air Terminal with corrosion resistant stainless chrome body made up of AISI 316 grade of height 0.50 metres capable of working in hazardous atmosphere, non-radioactive, fully autonomous (no battery, no external power supply is required), collects energy from the ambient electric field, CPRI tested with Radius of protection of 86 Metres and LPL of Level II. | 1 | No. | 350000 | 350000
3 | (b) | Supply of Standard / Special Mounting structure of height 4.5 mts. pipe, and 300 x 300 x 8mm MS plate, 3 mts. 48mm OD class C GI outer Pipe, 1.8 mtr,38mm OD inner PiPe, for roof mounting on concrete base and with FRP adapter. | 1 | No. | 75000 | 75000
3 | (c) | Supply and run of 25mm x 6mm with necessary clamps / supports for earth connection GI Flat Down Condutor on wall / floor / ground. | 200 | Mtr | 200 | 40000
3 | (d) | Supply of Test Link Box for each Down comer to disconnect the earth termination measurement of resistance conductor in order system to enable | 2 | No. | 3000 | 6000
3 | (e) | Supply and insallation maintenance free Gl Earthing System comprising of 50mm dia and 2 mtr. long earth electrode of low carbon steel rod with 100 micron bonding and 25 kgs. of carbon based environment friendly backfill compound and suitable clamp including earth pit | 2 | Each | 10500 | 21000
2 | 7.10 | Supplying & installation of heavy gauge PVC Open conduit pipe 32mm dia and 2.5mm thick confirming to IS 2509 with suitable size bends, junction boxes,adhesive paste etc, and fixing using inverted wood plugs in case of RCC ceiling and RCC wall stone structure or rawl plugs in case of brick walls using heavy gauge saddles at an interval of 700mm using WF screws and cement plastering damaged portion including wiring, modular switches, fan regulator, plug & sockets
3 | (a) | Primary point from lighting panel to modular switch box for Lighting and ceiling fan circuits | 50 | Mtr | 500 | 25000
3 | (b) | Point wiring from lighting panel to modular switch box for receptacle circuits | 50 | Mtr | 500 | 25000
3 | (c) | Secondary point from tapping point to Light and fan points | 100 | Mtr | 550 | 55000
4 | i) | Medium point above 3m and up to 6m | 50 | Mtr | 650 | 32500
4 | ii) | Long point above 6m and up to 10m | 30 | Mtr | 700 | 21000
3 | (d) | 1200mm high breeze ceiling fan with regulator (on switchboard) | 2 | No. | 5000 | 10000
3 | (e) | Supply, istallation and testing/commissioning of 18" (450mm) ISI, 900 RPM Heavy duty 415V, 3Phase exhaust fan with metallic blades with Mark. Makes: Crompton / Almounard / Havells Turbo Force | 3 | No. | 3000 | 9000
2 | 7.11 | Supply, Installation, Testing and commissioning of safety procedures for Electrical Equipments as per scope, specification and drawings.
3 | (a) | Supplying Electrical rubber mat tested to 22kV, with grooved ISI mark, 1.0m x 1.0m x 0.021m | 1 | No. | 30000 | 30000
3 | (b) | Supplying fire extinguisher with connected accessories complete, 4Kg mono Ammonium Phospate powder 50, stored pressure type, pressure guage. Gross weight 3.6Kg, empty weight 1.6Kg, can height 344mm, dia 108mm, discharge time less than 8 secs. With controllable discharge mechanism includng 5 years warranty with instalert system complete as per specification | 1 | No. | 10000 | 10000
3 | (c) | Supplying fire extinguisher with connected accessories complete, Mechanical foam type 9.0 litres | 1 | No. | 16500 | 16500
3 | (d) | Supplying rubber hand gloves conforming to IS | 1 | pairs | 6500 | 6500
3 | (e) | Supplying of first aid box | 1 | No. | 5000 | 5000
3 | (f) | Supplying and fixing of shock treatment chart on the wall with inside plastic sheet cover and plywood back plate frame work complete | 1 | No. | 3000 | 3000
3 | (g) | Supplying and fixing of danger board made out of MS sheet metal with two coats of non corrosive enameled paint | 2 | No. | 10000 | 20000
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 2078828

## SOD
BIDDER QUOTED PRICE
CONTRACT CP-07 : SUPPLYING, FABRICATION AND LAYING OF CLEAR WATER TRANSMISSION MAIN FROM T.K.HALLI TO HAROHALLI
SCHEDULE OF DAYWORKS
Level | Item No. | Description | Quantity | Unit | Rate (Rs.) | Amount (Rs.)
Note:The Contractor is to enter below the fully inclusive rates which he will charge for works carried out on a day work-basis. These rates are to cover for all overtime, subsistence and condition payments, transport of labour, supervisory cost and expenses, overhead charges and profit, waste, fuel, power, water and other consumable stores,use of all hand and pnemuatic tools, light and non-mechanical plant use of rail tracks, roads, scaffolding, staging, pumps, pipelines, hoists, derricks or cableways erected or in the operation for other purpose and used incidentally, spares and maintanance to plant, all as necessary for the purpose and efficient carrying out of the dayworks ordered. All quantities are provsional.
2 | 1 | Labour
3 | (a) | Unskilled Labour(man) | 1500 | Man Day | 325 | 487500
3 | (b) | Unskilled Labour(woman) | 250 | Man Day | 325 | 81250
3 | (c) | Tradesmen's helper | 500 | Man Day | 325 | 162500
3 | (d) | Carpenter and jointer | 50 | Man Day | 350 | 17500
3 | (e) | Plumber | 250 | Man Day | 350 | 87500
3 | (f) | Bricklayer | 50 | Man Day | 350 | 17500
3 | (g) | Drain Layer and pipe fitter | 250 | Man Day | 325 | 81250
3 | (h) | Electrician | 100 | Man Day | 350 | 35000
3 | (i) | Fitter | 250 | Man Day | 325 | 81250
3 | (j) | Mason | 125 | Man Day | 350 | 43750
3 | (k) | Bar benders and fixer | 250 | Man Day | 350 | 87500
3 | (l) | Watchman | 250 | Man Day | 350 | 87500
3 | (m) | Ganger | 350 | Man Day | 350 | 122500
3 | (n) | Chainmen and other personnel to assist Engineer's staff | 100 | Man Day | 350 | 35000
3 | (o) | Gascutter | 100 | Man Day | 350 | 35000
3 | (p) | Welder | 250 | Man Day | 350 | 87500
2 | 2 | Materials
3 | (a) | Diesel engine oil | 2000 | Litre | 65 | 130000
3 | (b) | Welding rods | 3000 | No. | 6 | 18000
2 | 3 | Construction Equipment
3 | (a) | Portable compressor with one tool and required length of hose 3 m3/min | 300 | Hour | 1650 | 495000
3 | (b) | Mobile crane (10 to 15 tonnes capacity) | 1000 | Hour | 1450 | 1450000
3 | (c) | Dumper / Tipper-5 cum capacity | 700 | Hour | 275 | 192500
3 | (d) | Generating set (33 KVA) | 150 | Hour | 345 | 51750
3 | (e) | Electric welding set including ancillary equipment and consumables | 250 | Hour | 475 | 118750
3 | (f) | -Do- oxy-acetylene gas cutting / gauging | 125 | Hour | 875 | 109375
3 | (g) | Loading shovel (1 m3 capacity) | 150 | Hour | 275 | 41250
3 | (h) | Dewatering pump with required suction hose, foot valve and strainer, delivery hose etc.
4 | (i) | 5 HP | 500 | Per day (8 hr shift) | 2200 | 1100000
4 | (ii) | 7.5 HP | 500 | Per day (8 hr shift) | 2600 | 1300000
4 | (iii) | 15 HP | 500 | Per day (8 hr shift) | 3200 | 1600000
4 | (iv) | 30 HP | 500 | Per day (8 hr shift) | 3800 | 1900000
3 | (i) | Concrete mixer (0.4/0.3 m3 capacity) | 250 | Hour | 225 | 56250
|  | SUB TOTAL |  |  |  | 10112875
|  | FEE (% OF SUB TOTAL) |  |  |  | 1415802.5
| TOTAL CARRIED TO GRAND SUMMARY |  |  |  |  | 11528677.5